## 2021 PRODUCTS
Revision | Revision 19 - 04/29/2021 | Revision 20 - 06/04/2021 | Revision 21 12/28/2021
Legend | Revision 22 6/26/2023
03 | CONCRETE
03 30 00 | Cast-in-Place Concrete | Concrete Patching Materials: Dayton Superior; Sika Corp.; BASF; Euclid Chemical Co. Vapor Barrier: A vapor barrier is required unless indicated otherwise by the soils report. 15-thick Mil. thick polyolefin or polyethylene resin-based geomembrane | Engineer or Contractor to select specific product types for the concrete repair required. Cast-in-Place Concrete as specified by Nevada Licensed Engineer of Record. Note: Concrete Moisture testing is required prior to installation of all Flooring Materials (except Carpeting).
03 35 10 | Polished Concrete Floor System | Basis of Design Product, L&M Concrete Systems (Laticrete) "Permashine". Consisting of 1) Sodium Silicate concrete densifier/hardener/dustproofer FGS Hardener Plus used over 2) Vivid Concrete Dyes - Fast drying dye for mixing with VOC compliant solvent (Alcohol preferred) to be applied before the densifier. 3) Petrotex siloxane fluoropolymer top coating blended with water based solution hardener, Oil/Acid Repellent, VOC compliant and compatible with chemically hardened floors. Floor Slab & Flatness Requirements (review with structural engineer to make sure no conflicts: Flattness: Overall FF40; Local FF30; Elevation reading per ASTM E 1155: Standard test method for determining floor flatness and levelness using the F-number system; ACI 117: Standard specification for tolerances for concrete construction and materials; ACI 302-8.15: Guide for concrete floor and slab construction. Hard Steel Troweled (3 passes) Concrete: No burn marks. Finish to ACI 302.1R, Class 5 floor. Natural Concrete Slump: 4-1/2 - 5 inches; Admixtures may be used. Minimum Concrete Compressive Strength: 3500 psi; no lightweight concrete Curing: Recommend - Damp Curing - 7 day-cure. Membrane forming curing compounds (ASTM C309, Type 1, Class B), all resin, dissipating cure. Acrylic curing and sealing compounds & polyethylene film are not to be used. | CCSD INCLUDED THIS ITEM AS AN OPTION to VCT FLOORING IF COST DIFFERENCE IS MINIMAL. NEW SCHOOLS - PERFORMANCE REQUIREMENTS: Cut Level (Depth of Cut) Grade 2 - Salt & Pepper Finish (roughly 1/16" cut of the surface). Shine Level: Level 3 (High Gloss, 1500 grit) gloss reading of 70 or higher; or Level B (semi-gloss, 800 grit) - gloss reading of 60-70 at a minimum. Caulk for Joints: Utilize custom colored poly-urea joint sealers tinted to match adjacent floor color. Caulk joints prior to polishing the concrete. Performance Criteria: National Floor Safety Institute (NFSI): NSFI Test Method 101-A Phase Two Level - High Traction Floor Abrasion Resistance: ASTM C779 Impact Strength: ASTM C805 Ultra Violet Light and Water Spray: ASTM G23-81 - No adverse effect to ultra violet and water spray. Reflectivity: 30% increase in reflectivity Meet - ASTM 1028 Co-efficient of Friction & ANSI 137.1 Slip Resistance Manufacturer's Certified Applicators required with at least 5 years documented experience installing polished concrete floor systems of the type specified. 10-Year Warranty Required. Protection Board is to be utilized to protect the surface of the polished concrete during construction.
03 47 13 | Tilt-up Concrete Walls | WaterProofing Additives: Euclid, Grace, Sika | Tilt-up concrete processes shall not mar the structural floor slab to remain. All bond breaking materials are to be removed from the finished floor slab following tilt-up concrete construction
04 | MASONRY
04 22 00 | Concrete Unit Masonry | CCSD Standard CMU: Standard Grey CMU Masonry to receive Paint Finish without water repellent additive. Integral Water Repellent: 2-part system for both CMU and mortar when CMU is not to receive paint finish: BASF - Masterpel 240 (CMU), 250 MA (Mortar); Euclid - Blocktite System; W.R. Grace Dryblock Un-glazed CMU Masonry (Plain, Split-Faced): Cemex, Superlite Block (ownes Tri Delta Inc.); Cind-R-Lite; Integral Colored CMU Masonry - acceptable Stains for CMU Masonry: to be determined Glazed CMU Masonry: Old Castle - Trenwyth Industries & Astra-Glaze; Spectra-Glaze II Most Schools have solid-Grout Walls: Supplied by Readymix producer as needed for project For CMU Masonry Penetrating Sealers used for Graffiti Resistance - please see Division 9: 09 96 23 | CMU Masonry stains are currently being evaluated - Euclid Chemical suggests we look for iron-oxide based stain with a penetrating sealer. 1/19/16 Construction Management Decision - Utilize standard gray CMU Masonry with a paint Finish in lieu of Split Faces Masonry and Glazed CMU Masonry.
04 23 00 | Glass Unit Masonry | Pittsburgh Corning, WECK (Vista Brick Solid Glass Block (Clear & Stipple finish)by Pittsburgh Corning) | Match existing products for modernization projects only
05 | METALS
05 10 00 | Structural Metal Framing including structural Steel | Structural Steel & Framing: As specified by Engineer of Record | Primed Steel must meet current indoor air quality code requirements; along with the VOC requirements.Submit compliance with VOC's and certify that no lead based paint is utilized.
05 20 00 | Metal Joists | Steel Joists: As specified by Engineer of Record Vulcraft ; SMI Joists Company; Valley Joist | Primed Steel must meet current indoor air quality code requirements; along with the VOC requirements.Submit compliance with VOC's and certify that no lead based paint is utilized.
05 40 00 | Cold-Formed Metal Framing | Cold-Formed Metal Framing: As specified by Engineer of Record Allied Studco; Knoor Steel Framing System; Consolidated Fabricators; National Gypsum; Dietrich | SJI Stds. Primed Steel must meet current indoor air quality code requirements; along with the VOC. Submit compliance with VOC's and certify that no lead based paint is utilized.
05 51 00 | Metal Stairs | Lapeyre Stair, Inc. (All-in-one welded unit, Aluminum Alternating Tread Design) | Unique tread design of this product sets it apart from other ships ladders - special cast aluminum treads support calf while stepping from tread to tread.
05 52 00 | Metal Railings | Handrails & Railings: as selected by Architect | Provide testing or documentation that railing design meets IBC requirements. No primed structural steel is to be used because it contains lead based paint. This includes beams, columns, cirders, bar joists, cold-formed metal framing, or any other structural component used in the construction of a school.
06 | WOOD, PLASTICS, AND COMPOSITES
06 40 00 | Architectural Wood Casework | Custom Casework: Anderson; Caseworx, Inc.; Classy; Form-A-Fab; Granite Mill; LSI Corporation of America (Approved for Science Labs); Stevens Industries; TMI Systems Design Corporation (Approved for Science Labs); Valley Custom Interiors, Inc.; Western Casework Plastic Laminate Manufacturers: Arborite Plus; Nevamar; Formica Corp.; Pionite; Wilsonart, Lamin-Art | AWI - American Woodwork Institute Compliance Required for All Casework. Provide Custom Grade Min. See Also Section 12 32 00
06 60 00 | Plastic Fabrications (FRP & FRL) | Pre-Finished Fiberglass Reinforced Laminate, FRL: Basis of Design - Panolam Surface Systems, Hard Stop** Fiberglass Reinforced Plastic FRP: Nevamar; Kemlite Co., Dudo Products, Lasco Composites LP, Hard Stop ** | Class A fire rating, high impact strength, suitable for high traffic areas and in wet areas, .075", meets ASTM E84, IMO Certified for marine Use. Green Guard Cold Certification. Wear Resistance - NEMA 3.13 - 3500. ** Utilize cement board backer behind locations to receive FRP & FRL. Provide FRL in toilet rooms and behind drinking fountains in lieu of ceramic tile. Provide FRP surround at custodial closet and type II finish on surrounding walls.
06 61 16 | Solid Surfacing Fabrications | Solid Surface Manufacturers: DuPont, Samsung
07 | THERMAL AND MOISTURE PROTECTION
07 01 50 | Urethane Elastomeric Roof Coating | Quest (United Coating) Elastuff 101-103; Roof-Mate - butter grade coating and polyester reinforcement by Quest
07 21 00 | Board Insulation | Gypsum Board (Thermal Barrier) - only required for Perforated Acoustical Deck: Non-Structural, moisture resistant gypsum panel, flat stock, 5/8" thick, 4 x 8 sheets: Type V Gypsum Board Polyisocyanurate Foam Roof Insulation (Induction Welded): Provide 2 layers of insulation with a prescriptive total thickness to meet R-30 requirements. For construction cost savings, the current adopted IECC code allows roof insulation R-Values to be set through Envelope Performance Calculations. Securock Roof Board by US Gypsum Co.; DensDeck by Georgia-Pacific Gypsum Corp. Securock Roof Board by US Gypsum Co. for use with Johns Manville; DensDeck by Georgia-Pacific Gypsum Corp. for use with Sika Sarnafil, Carlisle SynTec Corp. and Seaman Corp. ENRGY 3 by Johns Manville Roofing Systems Group - for use only with Johns Manville; Sarnatherm by Sika Sarnafil, Inc. - for use only with Sika Sarnafil, Inc. FTR-Value by Seaman Corporation - for use only with Seaman Corporation; Polyiso HP by Carlisle SynTec Incorporated. for use only with Carlisle SynTec Incorporated. | Closed Cell Polyisocycanurate foam core conforming to ASTM C1289, Type II, Class I. Meet flame spread of 75 or less according to ASTM E84 with minimum compressive strength of 20 psi according to ASTM C1289. Note: Air Barrier is not required at the roof deck; a cover board is not required.
07 21 16 | Blanket Insulation | CertainTeed; Johns Manville; Knauf Fiberglass Insulation; Owens-Corning
07 21 19 | Foamed-in-Place Insulation | Certainteed; Gago Western LLC; Demilec Inc.
07 41 13 | Metal Roofing | Rolled Seam Metal Roof Systems: Basis of Design - Butler Manufacturing Co. MR-24 standing seam roof system. Approved equal - Varco Pruden Buildings SSR Standing Seam Roof Systems. | Snap Lock or Batten type systems are not to be used. Roof Panel Requirements: 24-gauge x 2'0" nominal width, roll formed, Galvalume (aluminum zinc alloy coated steel) sheet coated on both sides with a layer of aluminum zinc alloy by continuous hot dip method (approximately 55% aluminum, 45% zinc). Triple spot minimum 0.55 oz. per square foot as determined by ASTM A 792. Length of panels shall be maximum possible to minimize / eliminate end laps. Butler panels shall have two major corrugations nominally 2" high not including seam, 24" o.c., and minor corrugations spaced 12" o.c. maximum between and perpendicular to major corrugations. Varco Pruden panels shall have two major corrugations nominally 3" high not including seam, 24" o.c., and striations running parallel between the major corrugations.
07 51 00 | Built-up Bituminous Roofing | Johns-Manville; Tamko; Fields; Conglas; GAF; CertainTeed | For Existing Rehab/ Modernization Projects only
07 54 00 | Thermoplastic Membrane Roofing | Reinforced PVC Single-Ply Roofing (Induction Welded): S327 Membrane by Sika Sarnafil, Inc.; Additional "or equal" products include: PVC Single-Ply Roofing (Induction Welded) with KEE (Ketone Ethylene Ester) polymer: JM PVC - Evaloy Membrane by Johns Manville Roofing Systems Group, Sure-Flex KEE HP Membrane by Carlisle SynTec Incorporated. Related roofing products as required by manufacturer for full-system warranty. Architect to provide RoofNav (FM Global) Approval numbers for the assemblies specified. Reinforced PVC Membrane (Induction Welded). Available Manufacturers: 1. Carlisle SynTec - SureFlex PVC Membrane 2. Johns Manville - JM PVC SD Plus 3. Sika Sarnafil - S327 Membrane 3. No substitutions allowed. Include related roofing products as required by the manufacturer for full system warranty. (On new construction projects, or new roofs from the original structural deck, the Architect is to provide RoofNav (FM Global) Approval numbers for the assemblies specified. RoofNav is not required on re-roofs or roof covers.) | Additional Criteria: 80-mil nominal, polyester reinforced, polyvinyl chloride (PVC) sheet membrane, ASTM D4434, Type III. Sheet width - 10' (3 meters). Membrane color shall be white and Energy Star rated, having initial reflectivity = 0.83 and initial emissivity = 0.90. Design Roof System for a 20-year life. 10 year warranty required. Note: Air Barrier is not required at the roof deck; a cover board is not required. Additional Criteria. Physical Properties: 80 mil =/- 4 mil (5%), polyester reinforced, polyvinyl chloride (PVC), ASTM D4434 with 5% mil variation. (membrane thickness will be measured and confirmed onsite.) Type III. Sheet width at 10'. Membrane color shall be white and Energy Star rated, having initial reflectivity = 0.90 and initial emissivity = 0.90. Design Roof System for a 30-year life. 20 year warranty required. (On new construction projects, or new roofs from the original structural deck, an air barrier is required at the deck; as well as a cover board under 80 mil membrane.)
07 60 00 | Flashing and Sheet Metal | Reglets: Fry Reglet Corp or for shop fabricated provide G-90 Material per ASTM A 653/A653M. Roof Flashing Assemblies: Acorn Engineering Co. Elmdor/Stoneman Galvanized Steel shall be 24 gauge, G-90 Material per ASTM A 653/A653M. Kynar Prefinished Steel Manufacturers: PAC-CLAD by Peterson Aluminum Corp; TUFFCLAD by Clad-Tex Metals; ColorKlad by Ryerson Inc., UNA-CLAD by Firestone or approved equal. Color to be selected from Manufacturer's standard colors. Continuous clips - where specified for use, shall be galvanized steel, one gauge thicker than the primary commponent being secured.
07 72 13 | Roof Curbs | Roof Curb Manufacturers: Roof Products, Inc.; Custom Curb, Inc; Thycurb Corporation or approved equal | Additional Criteria: Curbs shall be constructed using min. 18-gauge, galvanized steel with fully mitered and welded corners, non-canted base, integral base plates, internally reinforced with 1" x 1" x 1/8" steel angle (curbs with any side longer than 3'0"), factory insulated with 1-1/2" thick 3 lb. density fiberglass insulation, and factory-installed pressure-treated wood nailers. Min. height of curb shall be 8" above finished roof elevation. Curbs shall be constructed to match slope of roof and provide a level top surface for mounting of mechanical equipment.
07 72 33 | Roof Hatches | Hatches (Double Wall, Equip with Safety Post): Acudor; Milcor; Bilco; Precision
07 72 36 | Smoke Vents | Bilco or approved equal
07 84 13 | Penetration Firestopping | Firestopping Manufacturers: Specified Technologies; Hevi-Duty/Nelson; Hilti; Metaline/Metacaulk; Tremco; Nuco; 3M Sleeve Penetration Systems: ProSet Systems, Inc. or other manufacturer as indicated in Tested Penetration Assemblies. | Provide UL listed Penetration Assembly details (with current testing) on drawings.
07 92 00 | Joint Sealants | Joint Sealants: Hilti; General Electric, Sika Corp., Tremco, Masterseal, BASF, or approved equal HVAC Joint Sealants & Adhesives: Childers; Design Polymerics; Ductmate Industries, Inc.; Foster Products Corporation | Joint Sealant Standards: ASTM C1193 Standard Guide for use of Joint Sealants; ASTM C1472 Standard Guide for Calculating Movement and other Effects when establishing a sealant joint width. ASTM C920 86 for elastomeric joint sealants.
07 95 00 | Expansion Joint Cover Assemblies | Manufacturers: Balco, Inpro, Hyspan. Design expansion joints as required for installation; Provide a metal cover for all expansion joints per manufacturer's recommendations | Expansion joints without a cover are areas where bees create a hive or rats nest. Provide metal covers at all expansion joint locations.
08 | OPENINGS
08 11 13 | Hollow Metal Doors and Frames | Ceco ; Curries; Steelcraft | Exterior Doors: 16 gauge. Exterior Door Frames: 14 gauge - all HM frames to be full-throat welded. Interior Doors: 18 gauge. Interior Frames: 16 gauge. Interior Frames 4'-0" wade and over - 14 gauge. Fire Core Coor: provide as necessary for fire-protection and temperature-rise ratings indicated. Where indicated, provide doors fabricated with thermal-resistance value of not less than 4.0degF x h x sq.ft./Btu. All Interior Door Frames to be Flush with outside face of wall allowing the door to swing 180-degrees. For Door Hardware requirements see section 08 71 00
08 14 16 | Wood Doors | Marshfield Door Systems Inc. (Formerly Weyerhauser Co.), Eggers, Algoma, Graham, Buell, Oshkosh | Provide Hardboard Paint Grade Flush Wood doors to meet Architectural Woodwork Standards. Comply with IBC (Current Edition) Requirements and NFPA 80 for Fire-rated Doors. Provide particleboard core with faces bonded to the core utilizing a hot press; unless mineral composition core is required for a fire rating. Provide 5" block at top rail for closer and 5"x18" lock block at lock stile, and lock blocks at both sides of door if door is to receive panic hardware.
08 31 13 | Access Doors and Frames | BAR-CO, Division of Alfab; Bilco Company; J.L. Industries; Karp Associates, Inc.; Milcor, Inc.; Acudor; Cesco | Use stainless steel access doors or panels in wet areas or ceramic tile surfaces. Use painted doors in other areas. Conceal Hinges.
08 33 13 | Coiling Counter Shutters | Basis of Design - Cornell (Cookson) Model ESC10; Overhead Door Corp.; At Kitchen locations specify Stainless Steel #4 Counter Shutters; Face of Wall Mounting. Push-up operation, unless larger opening - specify electrical operation with bottom sensing bar and key operation. | Hardware for coiling counter shutters shall meet the requirements of Section 08 71 00
08 33 16 | Overhead Coiling Grilles | Basis of Design - Cornell (Cookson) VisionAire Model ESG10 or ESG12; Overhead Door Corp.; At Food Service Locations specify Stainless Steel Finish. | Hardware for coiling grilles shall meet the requirements of Section 08 71 00. Face of Wall Mounting. Standard Operation is Chain Hoist unless larger opening - specify electrical operation with bottom sensing bar and key operation.
08 33 23 | Overhead Coiling Doors | Basis of Design - Cornell (Cookson); Overhead Door Corp.; Exterior Locations: Cornell Model ESD30 Thermiser Max Insulated Rolling Doors; Meets IECC requirements; 22 ga. min. Exterior slat; 24 ga. min. interior slat & foamed-in-place insulation; thermally broken guide construction. Interior Locations: Cornell Model ESD10 Rolling Service Doors; min. 22 ga. slats. | Hardware for coiling doors shall meet the requirements of Section 08 71 00 Mounting: Face of Wall Mounting. Standard Operation is Chain Hoist unless larger opening - specify electrical operation with bottom sensing bar and key operation.
08 41 13 | Aluminum-Framed Entrances and Storefronts | ARCADIA, Inc.; EFCO Corporation; Kawneer Company Inc.; United States Aluminum Corp.; Vistawall Architectural Products; Peerless Products | Provide Thermally Broken Frames. All Aluminum Framed Doors shall have hardware meeting requirements of Section 08 71 00
08 44 13 | Glazed Aluminum Curtain Wall | ARCADIA, Inc.; EFCO Corporation; Kawneer Company Inc.; United States Aluminum Corp.; Vistawall Architectural Products; Peerless Products | Provide Thermally Broken Frames
08 45 00 | Translucent Wall & Roof Assemblies | Major Industries, Kalwall, or Approved Equal | Provide Manufacturer's complete assembly for standard 10 year warranty. Translucent Sandwich Panels to have UV Protection, Thermal Insulation, and Impact Resistance. Install within thermally-broken frames or as designed
08 51 13 | Aluminum Windows | ARCADIA, Inc.; EFCO Corporation; Kawneer Company Inc.; United States Aluminum Corp.; Vistawall Architectural Products; Peerless Products | Provide Thermally Broken Frames. Provide CCSD Security Coating on accessible windows only - 01/19/16
08 62 00 | Unit Skylights (Plastic) | Bristolite; WASCO | Mount Skylights on Prefabricated Curbs or customized as designed. Translucent Panels are to have UV Protection and Impact Resistance. Use manufacturer's standard polycarbonate.
08 62 23 | Tubular Skylights | Basis of Design - Solatube Commercial Series; Sun Optics | Provide Manufacturer's complete assembly for standard 10 year warranty. Provide dimming (black-out) capability with switch operation in rooms with tube skylights. Translucent Panels to have UV Protection and Impact Resistance. Use manufacturer's standard polycarbonate.
08 63 00 | Metal-Framed Skylights | Kallwall Corporation; Major Industries, WASCO, or approved equal | Mount Skylights on Prefabricated Curbs or customized as designed. Translucent Panels are to have UV Protection and Impact Resistance. Use manufacturer's standard polycarbonate.
08 71 00 | Door Hardware | Butt Hinges: Hager BB1168, BB1279; McKinney T4A376, T4A2714; Stanley FBB 168, FBB 179; Ives 5BB1HW, 5BB1 Continuous Hinges: Hager 780-210HD; McKinney MCK-22HD; Pemko FSHD; Select SL21HD; Ives 210HD; Select Door Closers – Elementary Schools: LCN XP 4040 Series; Norton 7500 Series Door Closers – Middle and High Schools: LCN 4040/4041; Norton Lock Cylinder and Keying-New Elementary Schools: Schlage Restricted Everest “D”; Sargent “N” Family of key sections Lock Cylinder and Keying – New Middle and High Schools: Schlage Everest “D” (See adjacent remarks.) Lock Cylinder and Keying-Modernization: All cylinders are to match existing site. Locksets and Latches – New Schools and Modernization: Schlage “ND 90” Series RHO (Vandalguard); Sargent FW10 line series Surface Bolts: DCI, Ives, McKinney, Rockwood, Trimco Automatic Flushbolts: DCI; Ives; McKinney, Rockwood, Trimco Exit Devices – Elementary Schools: VonDuprin 98/99 Series; Sargent 80 Series with CCSD modifications; Detex 10 or 40 Series | NO SUBSTITUTIONS Schlage-All locks and cylinders will be supplied in Schlage Restricted Everest "D" interchangeable core or Sargent "N" utility-patented keyway, with proper signatures to ensure that the integrity of the keying system shall not be compromised. Key blanks available only from factory-direct sources, not from after-market key blank manufacturers. Secured Delivery to CCSD Representative - Please contact Keith Anderson: CCSD Lock Shop @ 702-855-6680 x5161 (kaanderson@interact.ccsd.net) for Key Schedule approval and delivery instructions prior to ordering keys and permanent cores. Provide reinforcement in walls to receive door stops. No Drywall screws or plastic anchors allowed.
08 71 00 | Door Hardware Cont. | Exit Devices – Middle and High Schools: VonDuprin 98/99 Series Anti-Vandal Trim: Ives, McKinney, Seargent, Trimco (Match Exit Device) Push and Pull Plates: Ives, McKinney, Rockwood, Trimco Overhead Stops & Holders: Glynn Johnson; Rixson; Sargent Electromagnetic Door Holders: LCN, Rixson, RSG Edwards #150Y AQ 24V Thresholds: McKinney, NGP, Pemko, Zero Seals & Bottoms: McKinney, NGP, Pemko Zero Wall Bumpers and Stops: Quality; Glynn Johnson; H.B. Ives; Rockwood; Trimco Silencers: Ives, McKinney, Rockwood, Trimco Latch Guards: DCI, Ives, McKinney, Rockwood, Trimco Kickplates: Ives, McKinney, Rockwood, Trimco Door Stops and Holders: Corbin; Glynn Johnson; Rixson; Firemark; Trimco (School Version) Key Cabinets: Lund, Telkee, HPC NO OTHER SUBSTITUTIONS WILL BE ALLOWED | Keys: Existing factory registered master key system.Construction keying: furnish temporary keyed-alike cores. Furnish 10 construction keys.Furnish 2 construction control keys.Furnish 100 Key Blanks. Key Cylinders: furnish utility patented, 6-pin solid brass construction. Cylinder cores: Furnish cores combinated at the factory of the lock manufacturer, where permanent records are maintained. Locks, keys and cylinders/cores shall be of the same manufacturer. Furnish 20 of each type and keyway zero-bitted cores. Permanent keys: use secured shipment direct from point of origination to Owner. Provide: 4 keys per cylinder, 8 master keys per group, 12 grand-master keys, 3 control keys. Bitting List: Use secured shipment direct from point of origination to Owner upon completion. Factory Bitting List, hard copy and electronic copy, shall cross reference the keyset symbols with the architectural door numbers and the Clark County School District Room Numbers. Deliver permanent cores, permanent keys, key blanks and Bitting List to CCSD Lock Shop in a single shipment. Label cylinders and cylinder housings with key symbols using manufacturer’s standard labeling method.
08 80 00 | Glazing | Float Glass Manufacturers: Guardian Industries; PPG; Pilkington; Saint Gobian; Visteon Float Glass Fabricators – Tempered, Non-coated Insulated: TruLite; Glasswerks, Oldcastle Glass; ACI; AFGD; Hehr Glass; Northwestern Industries; Glazing Sealants: as required window system manufacturer. Zero/International INO Coated Fabricators Insulated Glass: AFGD; Guardian Industries Corporation; Interpane; Northwestern Industries; Oldcastle Glass; Viracon Custom Laminated/Security Glass: Globe Amerada; Hehr Glass; Northwestern Industries; Oldcastle Glass Lexan: (Polycarbonates); Architects to submit manufactures to CCSD for approval. Fire Rated Glass Products:(If Required) InterEdge Technologies; SAFTI, O’Keefe’s; Technical Glass Products; Vetrotech-Saint Gobain
08 91 00 | Louvers | Metal Wall Louvers: Airolite Co.; Construction Specialties; Industrial Louvers, Inc.
09 | FINISHES
09 21 16 | Gypsum Board Assemblies | Georgia Pacific, National Gypsum, U.S. Gypsum Company; Pabco; Gold Bond, Domtar Gypsum, Louisiana Pacific | Backing Board Requirements for all Toilet Rooms & Janitorial Rooms containing Mop Sinks: Provide cement board up to 3'-0" above finish where fixtures are located. Seal cement board at the floor with a bead of silicone caulk. Cement Board is required on both sides of walls. Classroom Sink Locations: Provide Cement Board on each side of the wall; up to 3'-0" above finish floor where sink is located; extending 8'-0" in length on each side of the centerline of the sink. Seal cement board at the floor with a bead of silicone caulk. Support Backing in Walls required for: Architectural Woodwork & Casework, shelving, toilet accessories, railings & handrailings, grab bars, mirrors, marker & tack boards, draperies, wall mounted light fixtures, door stops, and all other wall mounted items.
09 22 13 | Metal Furring | Metal Furring & Lathing: US Gypsum; Alabama Metal Industries; K-Lath-Tree Island Industries
09 22 16 | Non-Structural Metal Framing | Allied Studco; Cemco Steel Dietrich; Knoor Steel Framing Systems; Trackloc
09 24 23 | Portland Cement Stucco | Allowed as an exterior finish material - per architect's 3/4" or 7/8" performance specification
09 28 00 09 29 82 | Backing Boards & Underlayments; Gypsum Board Fireproofing | Gypsum Drywall Systems: U.S. Gypsum Company; Pabco; Gold Bond; Domtar Gypsum; Georgia Pacific; National Gypsum. Use cement backing board in wet areas. | See Also - requirements of 09 21 16 and Division 7 Sections.
09 22 36 09 22 39 | Metal Lath and Veneer Plaster Base | Plaster: Gold Bond Building Products Division; National Gypsum; Thoro Products; US Gypsum Company, Georgia Pacific Lath - Amico, Cemco, Phillips Manufacturing)
09 31 00 | Thin-Set CeramicTiling | Wall Tile: American Olean; Dal-Tile Corporation; Florida Tile; Summitville Tile; Morena; Monarch; Interceramic Tile & Stone Gallery Mortars and Grouts: Laticrete International; Mapei; A.O.; Bostik; | Utilize Fiber-Reinforced Plastic and Pre-Finished Fiberglass Reinforced Laminate in lieu of Ceramic Tile for walls in toilet rooms and at janitorial sink locations. See Section 10 26 23.
09 32 13 | Mortar-Bed Ceramic Tiling | Floor Tile: Monarch Tile; Marine; American Olean; Dal-Tile; Florida Tile; Morena; Interceramic Tile & Stone Gallery Mortars and Grouts: Laticrete International; Mapei; A.O.; Bostik; Dal Tile | Utilize Resinous Flooring, section 09 67 23 for Toilet Room and Food Service Floors
09 32 16 | Mortar-Bed Quarry Tiling | Quarry Tile: Monarch Tile; Marine; American Olean; Dal-Tile; Florida Tile ; Morena ; Interceramic Tile & Stone Gallery Mortars and Grouts: Laticrete International; Mapei; A.O.; Bostik; Dal Tile | Utilize Resinous Flooring, section 09 67 23 for Toilet Room and Food Service Floors
09 51 13 | Acoustical Panel Ceilings | Acoustical Panels: Armstrong; Celotex; USG Interiors Suspension System: Armstrong World Industries; Chicago Metallic Corporation; USG Interiors - Donn Suspension System; Celotex Brand Ceiling Suspension Systems
09 68 13 | Carpet | CCSD Approved Carpet; Basis of Design: Tandus Centiva 6-foot wide Powerbond; Antron Lumina 6.6 Fiber, 18 oz tufted weight; with Fluorochemical stain protection & anti-microbial treatment. TARR Rating > 3.5 Super Severe. Backing system - closed cell Vinyl Cushion, 25.5 oz/sq yd, moisture barrier, synthetic thermoplastic polymer backing designed for chemically welded seams. CCSD Approved Walk-Off Carpet: Tandus Centiva monolithic Tufted Pattern Loop Pile or textured multi-loop tile; 100% solution dyed TDX Nylon, 20-22 oz Tufted Weight, with Fluorochemical stain protection & anti-microbial treatment. TARR Rating > 3.5 Super Severe. Backing system same as above. Adhesives: Tandus Centiva RS Peel and Stick backing or wet adhesive consistent with the results of Relative Humidity Testing. | CCSD Carpet is Owner Furnished. Installation to be as directed by CCSD. CCSD is considering a change in the carpet pattern from "Confetti" to Tandus Centiva "Aftermath II". 24 x 24 Carpet Tile is also under consideration.
09 64 53 | Resilient Wood Flooring Assemblies | Basis of Design: Tarkett "Clutch Court" - Hardwood Maple Floor Surface over 2 (solid) layers of plywood and manufacturer's standard shock absorbing material: Clutch Court - 70 durometer, 3/4" conical shaped pad. Other Manufacturer's include: Robbins, Inc.; Horner Flooring Co.; Connor - Sports Aacer Flooring, LLC; Action Floor Systems, Inc.; Premier Hardwood Products Inc.; Prestige Sport System, Superior Floor Co., Inc. | Substrate Flattness: Concrete or other substrate Flattness Criteria must meet ASTM F710, ACI 302.2R, along with manufacturers requirements.10 year manufacturer's comprehensive coverage warranty. Product Criteria: Maple Floor surface must use MFMA certified finishes; 2nd or better maple grade; Must meet ASTM F2772, Force Reduction - Class 5; Ball Rebound - Pass; Random Plank Length. Plywood - 15/32" double Layer, 3-Ply CDX Grade APA.
09 65 19 | Resilient Flooring & Base | Vinyl Composition Tile: Armstrong World Industries; Azrock Industries; Tarkett Inc.; AB Color Plus; Rickett Quartz Rubber Base: Nora Systems, Roppe, Johnsonite Luxury Vinyl Tile (LVT): Tarkett: Tandus Centiva-Contour Series | Rubber Base may be furnised by CCSD as directed. Relative Humidity Testing utilizing probes at 40% of the slab depth per ASTM F-2170 for the concrete slab is required prior to installation of product. Manufacturer's RH level requirements and installation guidelines must be met prior to installation.
09 65 19.33 | Rubber Tile Flooring | Homogenious Rubber Sheet & Tile: Mowhawk Group - True Collection; Nora Systems, Roppe, Johnsonite | Interior Stair locations where appropriate for use. Include stair treads, risers, and nosings including visually impaired configuration. Products must meet ADA slip resistance requirements (and per ASTM D-2047) Additional Criteria: 3 mm gauge, ASTM E-84 smoke developed and flame spread requirements for exit enclosures; Hardness ASTM 2240 - Shore A; > 85; Classification ASTM F-1344, class 1 - A; ASTM 1515 - resistance to light exposure; Abrasion Resistance - ASTM D3389 <1; Provide 10-year warranty.
09 65 66 | Resilient Athletic Flooring | 8mm Rubber Surface with EPDM Color Chips - Mondo USA; Tarkett Commercial Athletic Floors - Drop Zone; Glue Down Adhesive preferred for interlocking tiles. | Weight Room locations. Installation guidelines include ASTM F710, ACI 302.2R. Relative Humidity Moisture Testing is required. Use Full Adnesive up to 92% RH per ASTM F210; Use moisture barrier if moisture tolerance is between 92% - 98%. 3-year comprehensive warranty required.
09 67 23 | Resinous Flooring | Provide Urethane System at Food Service Locations (Kitchen and Food Service/Storage) and Epoxy System at Toilet room Locations; The Stonhard Group: Stonshield Products. Urethane Coating System - StoncladUT: 1) provide urethane moisture barrier - Stondri MVT ; 2) Primer: Stonclad UT has a self-priming Trowel Urethane Coat 3) Trowel Urethane Coat: Stonclad UT polyurethane mortar system consisting of poly-urea binder, pigments and fine quartz aggregates (Stone Shield Aggregate); 4) Stonclad Urethane UT7 Finish Coat (Gloss Finish): two-component, tinted urethane coating specifically formulated to provide protection from chemicals and increase abrasion resistance. Provide one coat with medium texture finish. At locations below stationary food service equipment provide a second coating for a smoother finish that enables cleaning under equipment. Cove Base required: StoneClad UR4 Epoxy Coating System - Stoneshield HRI: 1) Provide two-component, high solids, epoxy moisure barrier Stondri MVT 2) Manufacturer's standard penetrating epoxy primer 3) Trowel Epoxy Stonshield HRI Base: three-component, troweled mortar base consisting of epoxy resin, curing agent and finely graded silica aggregate, provide cove base 4) Epoxy Undercoat - Stonshield Undercoat: three-component, free flowing epoxy formulation consisting of resin, curing agent 5) Broadcast fine aggregates (Stoneshield Aggregates) 6) Clear Epoxy Sealer - Stonkote CE4 (Gloss Finish): Two-component, high performance, UV resistant clear epoxy sealer with Medium texture finish. | Provide resinous flooring systems at toilet room and kitchen areas to meet requirements of the Clark County Health Department. Must also resist acid-staining and thermal near cold/hot food storage. Coating Systems shall be 3/16" to 1/4" thickness. Surface Texture: Medium Texture - Coefficient of Friction per ASTM D2047 to be .7 - .8. Provide manufacturer's standard 6" cove product compatible with coating system specified. Utilize Cement Backing Board behind cove base up to 12" above finish floor. Urethane Standards: Compressive Strength (ASTM C579) - 7,700 psi; Flexural Strength (ASTM C580) - 2,400 psi; Tensile Strength (ASTM C307) 1,000 psi; Hardness (ASTM D2240, Shore D) 85-90; Flammability (ASTM E-648) - Class I; Thermal Coefficient of Linear Expansion (ASTM C-531) 1.1 x 10 to the -5th power degrees F. Epoxy Standards: Compressive Strength (ASTM C-579) - 10,000 psi; Tensile Strength (ASTM C307) - 2,000 psi; Flexural Strength (ASTM C580) - 4,300 psi; Flexural Modulus of Elasticity - 2.0 x 10 to the 6th power, psi; Hardness (ASTM D2240, Shore D) 85-90; Flammability (ASTM E-648) - Class I; Thermal Coefficient of Linear Expansion (ASTM C-531) 1.3 x 10 to the -5th power degrees F.
09 68 16 | Sheet Carpeting | 6' Hybrid Resilient Carpet Flooring with Cushioned Back: Tandus Centiva Powerbond Hybrid Resilient Floor RS. Level loop, woven, 100% solution-dyed Nylon, type 6.6 Antron with "Ensure" soil release capabilities, 18 oz.yd.; .0117 Pile Fiber Height, 7488 Pile Density, 1/13 Pile Gauge; 8.2 Stitches per inch; 104.96 Tufts/sq. in; 16" Pile marker spacing. Closed cell Powerbond Cushion. No delamination per ASTM D-3936. Choose from three standard colors clay, moss, denim. Peel & Stick Installation (RS) typical or acrylic sealer as recommended by manufacturer. Walk-0ff Carpet: Tandus Centiva Powerbond Abrasive Action II - Resilient Floor RS. Color: Charcoal; Patterned Loop, 24 oz/sq.yd.; 1/12 Gauge; 8 stitches per inch, 96 tufts/sq.in.; Pile Height Ave. 0.187 inch; Pile Thickness 0.115 inch; 7,513 oz/cu yd Density FactorTDX Nylon; 100% Solution Dyed; Ensure Soil/Stain Protection; Synthetic non-woven tufting substrate. | Owner Furnished. Must Pass ASTM D-2859 for surface flammability, Smoke Generation - less than 450 per ASTM E-662; less than 3.0 kV (AATCC 134) Permanent Conductive Fiber; TARR Rating >3.5 Super Severe
09 72 00 | Wall Coverings | Wall Coverings are not to be utilized - Paint Finish is acceptable | Vinyl coated wall fabrics used previously are coming apart at the seams - this product is being removed in existing schools.
09 77 00 | Special Wall Surfacing | See Section 06 60 00 for RFP Manufacturers
09 84 33 | Sound Absorbing Wall Units (Fabric Wrapped Acoustical Wall Panels) | Tackable Acoustic Wall Panel: Gilford of Maine - Basis Design; Decoustics; Armstrong World Industries, Inc.; Sound Concepts Canada, Inc.; Wall Technology, Inc. - TK 125 WP-C; Conwed; Lamvin; Sound Seal; Quiet Technology Systems; SoundStop® Tackable Wall Panels Acoustical Wall Panels: Tectum - Basis Design; MPC, Inc.; Wall Technology; Conwed; Decoustics; G&S Acoustics; Lamvin; Quiet Technology Systems; Sound Seal | Tackable Acoustic Wall Panel: Gilford of Maine - Basis of Design NRC Min. 75 per ASTM C423; must meet ASTM E84 25/450 flame spread/smoke developed criteria. Flame Retardant treatment is required. Provide fabric covering. Acoustical Wall Panels: 1-1/8" thick, width and height by Architect. Must meet ASTM E84 25/450 flame spread/smoke developed criteria. Flame Retardant treatment is required. Provide paint finish.
09 84 36 | Sound-Absorbing Ceiling Units | Acoustical Ceiling Panels: Tectum - Basis Design; | Tectum, Inc. Finale Panel, approx 2" thick 47"-high x 120"-long; beveled edges, NRC Min. 75 per ASTM C423; must meet ASTM E84 25/450 flame spread/smoke developed criteria. Flame Retardant treatment is required. Provide paint finish.
09 91 00 | Painting | Paint Manufacturers: Sherwin Williams (Frazee Paints); Dunn Edwards Paints; ICI Paints; Vista Paint - Midgrade "or equal" to products listed, Semi-Gloss. Paint Quality Standard: Mid Grade products are approved as follows: Interior Primer: Dunn Edwards Vinylastic (new drywall); Sherwin Williams & Frazee: Drywall Primer and PVA Primer Interior Semi-Gloss Enamel: Dunn Edwards: Spartawall & Spartazero; Sherwin Williams: Pro Mar 400 Zero (Frazee: Endurable) Interior or Exterior Primer: Dunn Edwards:Ultra Grip; Sherwin Williams & Frazee: Grip & Seal Interior or Exterior Semi-Gloss Enamel: Sherwin Williams: Solo (Frazee: Endurable) Exterior Semi Gloss Enamel: Dunn Edwards: Spartshield; Sherwin Williams: Solo (Frazee: (Endurable) Exterior Flat (Flat should only be used on exterior non-accessible areas): Dunn Edwards: Spartshield; Sherwin Williams: A 100 Flat (Frazee: Duratec II) Interior & Exterior Doors & Frames (Semi-gloss): Dunn Edwards: Aristoshield; Sherwin Williams: Aro-Thane (Frazee: Aro-Thane) | CMU Masonry or Concrete Waterproofing/Graffiti Coating: See Section below 09 96 23
09 96 23 | Water & Graffiti Resistant Coatings (Note - paint finish is preferred) | Masonry Weather Seal & Graffiti Coatings (must contain silane or siloxane): Prosoco - Sure Klean Custom Masonry System or approved equal; Used only for CMU Masonry or Tilt-up Concrete with integral water repellants. Paint finish is preferred. | Single component, solvent based products (for compatibility with CMU masonry or Tilt-up concrete integral water repellants. Penetrating, stain resistant breathable coating must be appliedaccording to manufacturer's pre-printed instructions.
10 | SPECIALTIES
10 11 00 | Visual Display Units (Marker & Tack boards) | Manufacturers: NACO/GSI; Lemco; Platinum Visual Systems; Claridge; Shanahan’s Ltd.; Newline Products; Polyvision, Egan Additional Requirements - Marker Board: 4' x 8' or 4' x 4' as indicated in Education Specifications;. Marker Trough: 2-5/8 inch blade type aluminum marker trough, continuous full length of board Maprail: 1 inch high, continuous full length of board. Map Hooks: Provide Two (2) map hooks with hook and metal spring clip per 4 feet of board length. Flagholder: Provide One (1) flagholder per room. Concealed, mechanical mounting. Finish: Low gloss white porcelain over steel board with clear anodized trim. | Construction: Porcelain Enamel over steel markerboard, 28 gauge steel sheet to meet ASTM A424, Type I commercial Quality. Aluminum Extrusions ANSI/ASTM B221 Materials: 7/16" particle board with .015 aluminum foil backing core. TackBoard Requirements: 4' x 8' or 4' x 4' Size as indicated in Education Specifications; Cork: Fine grain natural cork, homogeneous composition.
10 14 00 | Signage | Etched Metal: Vision Mark, Inc.; Advance Insignia; Insignia, Inc. Aluminum Letters: A.R.K. Ramos; Gemini Inc.; cast brushed aluminum letters. Metal Signs: A.R.K. Ramos; Metal Letters; Metallic Arts Inc.; Gemini; Metal Arts; Signmasters | Lettering Stype shall be Helvetica Medium. Provide Directional Signage; Accessible Signage (including interior & parking signs);
10 21 13 | Toilet Compartments - Solid Color Reinforced Composite Toilet Compartments | Scranton Products (Comtec/Santana/Capitol Partitions) - "Hiny Hiders" Floor Mounted Overhead Braced System & Urinal Screens; PSiSC (Columbia) - system to match Scranton Products. Hardware Requirements: All extruded aluminum to be heavy duty 6065-T5 Alloy. Overhead Rail - 1-1/2" x 1-1/4" heavy duty extruded aluminum Headrail; Brackets: 54" Continous deavy duty extruded aluminum; Strikes: 6" heavy duty extruded aluminum (inswing or outswing); Standard Stall Hinge: 8" heavy duty extruded aluminum; Accessible Stall Hinge: 304 stainless steel piano helix hinge with edges welded and ground; Latch with Emergency Access Capibility: Heavy duty extruded aluminum with brite 50 anodized finish, black anodized 304 cast slidebar & button; Coat Hook: Heavy duty chrome plated aluminum Zamak; Pilaster Shoe: 3/4-inch thick High Density Polyethylene NOT stainless steel. | Doors, panels & pilaster: 3/4-inch thick High Density Polyethylene (HDPE) resins & pigments with edges rounded to 1/4" radius. Specify Manufacturer's 25-year warranty against breakage, corrosion, and delamination. Configuration, dimensions, mounting heights, accessory locations and hardware locations shall be in accordance with ANSI 117.1 and the latest ADA law.
10 21 23 | Cubicle Curtains and Track | Clickeze Corp. (Basis of Design), C-S Group, Imperial Fastener, AR Nelson | Track: Provide 6065-T5 Extruded Aluminum Track, provide corner bends, splices, end caps and accessories. Carrier: 2 wheel roller-type carrier with stainless steel hooks (3 ea. Per foot of track) and chain assembly to hang curtain; Mounting: 4-inch pendant mounts for gypsum board ceilings; surface mount track at lay-in ceilings. Color: White Cubicle Curtains: 100% polyester, pre-shrunk, yard-dyed, permanent flame proof; anti-microbial treated; with stainless steel eyes in top hem for hanging. Top 18" of material to have heavy nylon. Curtain Size: Size so bottom is 12 to 15-inches above floor by length of track for complete closure.
10 22 13 | Wire Mesh Partitions | Style 840 - Wire Crafter, Inc.; Sure Guard Panel Inserts - The GS Co.
10 22 33 | Accordion Folding Partitions (Fabric-Wrapped) | Manufacturers: Modernfold (Soundmaster SM12), Panelfold (Fabricwall STC 40), Hufcor (Accordion Door Model 4100) - System similar to Panelfold Fabricwal accordion partition, side stacking, rounded folding partitions with heavy duty textured vinyl wall covering & polyester backing. Include framework carriers, track, and all accessories necessary for a complete installation. | STC 40 min. Design, provide and coordinate structural support for folding partition. Provide storage pocket. Used for flexible classroom spaces that are opened more frequently. Approx. weight of panels 5 lbs/sq.ft. Fire Hazard Classification - ASTM E84, Class A.
10 22 39 | Folding Panel Partitions (Operable Partitions) | Manufacturers: Modernfold - Acousti-Seal No. 931 - Encore 52 STC; Hufcor - Omni-Directional Panels, Model 641; Panelfold - Series 800 | 4" thick, STC 52-56 or higher. Design, provide and coordinate structural support for folding partition. Used in openings that are opened less frequently and need higher STC requirements (stage/music separation). Weight of panels approx 13.6 lbs/sq.ft.; Fire Hazard Classification - ASTM E84, class A. Provide storage pocket.
10 26 13 | Corner Guards (Wall and Door Protection) | Arden Architectural Specialties; Acrovyn; Balco, Inc.; Korogard – Koroseal; IPC Door and Wall Systems; Pawline Pro-Tek | Aluminum and Stainless steel corner guards
10 26 23 | Protective Wall Covering (FRP & FRL) | Refer to Section 06 60 00
10 28 13 | Toilet Accessories (Toilet, Bath, and Laundry Accessories) | Manufacturers: Bobrick Washroom Equipment; Bradley Corporation; Gamco Equipment; McKinney/Parker; Continental Accessories to be specified include: Sanitary Napkin Dispenserl; Toilet Partition & Shower Grab Bars. and shower seat to meet ADA law; Mop Strip, Mirror, Robe Hooks, Shower Curtain Rod and Vinyl Curtain, Wall mounted baby changing station. | Toilet Accessories provided by CCSD include: Paper Towel Dispenser: SofPull Mechanical Handwound Roll Towel Dispenser (Georgia-Pacific, #59489); Toilet Tissue Dispenser: Compact Side-by-Side Double Roll Bathroom Tissue Dispenser (Georgia-Pacific, #56784. Include accessile school mounting requirements for these products along with other products specified. Soap Dispenser: 2000 ml capacity, screw attached to backplate mounting. GOJO (No. GOJ5161-03): FMX-12 Foam Handwash Soap Dispenser - Manual;
10 41 16 | Emergency Key Cabinets | Provide 1 ea. Knox box at the front entrance to the school. The Knox Co. Series 3200-Knox Box.
10 43 13 | Defibrillator Cabinets | Owner Furnished Owner Installed after school is opened
10 44 13 | Fire Protection Cabinets | Standard Locations: Larson Model FS 2409-R4 (for 4” stud walls or smaller) or 2409-R6 (for 6” stud walls) Kitchens with Deep Fat fryers in the Cooking Line: Larson Model FS 2712-RM | All models will have: a) Steel horizontal Duo Doors; b) 1/8 acrylic glazing; c) Larson Lock with recessed pull handle. CCSD provides and installs the fire extinguishers.
10 51 13 | Lockers | Academic Metal Lockers: DeBourgh Manufacturing Co.; List Industries, Inc.; Penco; Lyon Athletic Metal Lockers: DeBourgh Manufacturing Co.; List Industries, Inc.; Penco; Lyon Lockers - Combination Locks for Student Lockers: Master 1654; Zephyr 1954
10 51 53 | Locker Room Benches | Locker Room Benches: Santana Products Co., Inc.; Capitol Partitions; Comsec Industries
10 56 29 | Storage Racks | Plywood Storage Rack: Broadhead Garrett, LM-200 Lumber Storage Rack: Broadhead Garrett, MC-2
10 57 00 | Wardrobe and Closet Specialties | Triple Fitting Mirror: LSI Model 9000 Coat Racks: Rack Model: Magnuson Group, FL-1/100 + 6 - 40-inch extruded aluminum hook strip with 6 black ABS Plastic Hooks.
10 75 13 | Flagpoles | Manufacturers: American Flagpole, John Ewing & Co., Pole Tech Company, Morgan-Francis | Crank Operated, Cone Tapered, Ground Mounted, 6-inch Dia", 30-foot tall, Aluminum Flagpoles with a cast-in place concrete base. Include Flag and related accessories. Gold Anodized Finial.
10 81 13 | Bird Control Devices | Manufacturers: Bird-B-Gone, Inc.; ABC Nixalite. Bird Spikes: Rigid one-piece construction; U.V. stabilized polycarbonate, heat and weather resistant - marine grade 316 stainless steel spikes; 1 to 3-inch; Width as required 1 to 8-inch x 2-foot sections. Number of Rows and mounting - as determined by manufacturer and based on project/site conditions. | Furnish products from one manufacturer for the entire project. Product shall carry a 10-year min. warranty against U.V. breakdown and stainless steel degredation. Installation shall be warranted for 2 years.
11 | EQUIPMENT
11 13 13 | Loading Dock Bumpers | Durable Mat Co.; Pawling Corp. | Standard reinforced rubber pads are utilized for Dock Bumpers
11 22 13 | Safes | Safes: Inground: AMSEC B1500 or B3800; Wall: AMSEC WS1214; Freestanding: BF2116 | Wall Mounted Safe: Recess wall safe such that safe flange is flush with the outside surface of the wall. Manufacturer rough opening requirements: 12-7/8"H x 14-1/2W x 10-1/8" Deep.
11 30 13 | Residential Appliances | Range Hood: General Electric (Model JV327X) Broan (Model 37308) Owner Furnished Residential Appliances: General Electric Co.; Frigidaire Appliance Co.; Sears Kenmore; Hotpoint; White Westinghouse; Amana; Scotsman | A/E team to coordinate space clearances, power, and other requirements to support Owner Furnished and Owner Installed Residential Appliances.
11 40 00 | Food Service Equipment | Coordinate Food Service Equipment & requirements, including layout with CCSD Food Services. Contact - Mario Saenz. (702) 799-8123 x5300; (702) 378-6835 Mobile; Large files can be sent to saenzm@nv.ccsd.net; msaenz@interact.ccsd.net | Refer to the basic layout of the prototype school involved; including equipment specifications and layout. Food Services is available for questions.
11 51 19 | Book Theft Protection Equipment | Dialoc-ID, Model Elipse | LCS-Pro
11 52 13 | Projection Screens | Projection Screen-Motorized: Da-Lite “Senior Electrol”; Claridge; Draper; Stewart Filmscreen Model B w/ Ultra Matif 800 Fabric Spring Roller Projection Screens: Da-Lite Screen Company; Draper Shade & Screen; Envoy - Draper Screen Co., Inc. Electronically Operated Screens: Da-Lite Screen Company; Draper Shade & Screen
11 52 16 | Projector | Refer to Appendix 27 41 16.51 for Audio Video Equipment and systems information. Classroom Projector: Hitachi Ultra-Short Throw Interactive (Smart) Projector: Model No. HITCPTW2505 (2700 Lumens); Model No. HITCPTW3005 (3300 Lumens). Projector Accessories: Finger Touch Module (#HITFT01); Super Booster USB Extender (#CBT29341); Wall Mounting Bracket (#HAS-WM05) ES Stage Projector: Model No. HITCPWX8265 (6500 Lumens) | Note: see projection screens (11 52 13) for locations utilizing rear projection.
11 61 33 | Rigging Systems and Controls | Stage Rigging: Protech; Stagecraft Industries ; J.R. Clancy Inc. Secoa Hoffand & Sons; H & H Specilities; Jason Industries
11 61 43 | Stage Curtains and Tracks | Stage Draperies (Fabric Manufactures): Milliken & Co.; J.B. Martin; K&M Fabrics | 100% Polyester IFR (inherently fire resistant) velour fabric including curtain and valance; weight not less than 25 ounces per linear yard with a pile height of approx. 120 mils. Provide Track, Draw Curtain Machine, and all components necessary for a complete installation.
11 66 23 | Gymnasium Equipment (Middle Schools) | Indoor Basketball: Jay Pro; Porter; A.D.P. – Lemco – 1335 Series; Arizona Courtlines; First Team Indoor Volleyball Posts: Senoh; Schelde – 67000 Series; Arizona Courtlines Wall Padding: Promat; Draper Inc.; Porter Athletic Equipment Co.; Resilite Manufacturing; Performance Sport Systems
11 66 43 | Interior Scoreboards | Interior Scoreboards - Basketball (Volleyball, Wrestling): Daktronics Model #BB-2155 size 6'-0" x 10'-0" - Full Electronic Captions used; Add team name in place of home; Horn to be model 55 Trumpet Horn; Nevco Model 2710 Fair-play Model #BB-3660-4 size: 5'-6" x 9'-0" (May Change) with full electronic captions; team name in place of home. | Single Sided LED Scoreboards to be utilized for interior locations. Each scoreboard shall be ordered with 120V AC plug-ins and Radio Control. Include hard side carrying case for storage. Utilize dark colors for sign backs.
11 66 23 | Gymnasium Equipment (High Schools) | Indoor Basketball: JayPro 800 KD Series; Porter 900 W Series; A.D.P. – Lemco 1335 Series; Arizona Courtlines Indoor Volleyball Posts: Schelde 67000 Series; Senoh; Draper PVS-01; Arizona Courtlines Mats: Porter Athletic Equipment Co.; Resilite Manufacturing Wall Padding: Promat ; Draper; Porter Athletic Equipment Co.; Resilite Manufacturing; Performance Sports System
11 68 13 | Playground Equipment (Elementary Schools) | Modular Playground Systems: Miracle Kids Choice – Modular Playground System; Playmaker – Play World Systems; Kid Builders - Little Tikes; Playbooster - Landscape Structures; Series 2000 - BCI Burke; Powerscape - Gametime; Play & Park Strucutures - Supermax Softball Backstop: L.A. Steelcraft - Model 810JH-4C (Basis of Design) Basketball Goals: L.A. Steelcraft; First Team Tetherball: L.A. Steelcraft (Design Basis - TBPCB); American Playground; UltraPlay Systems | Softball backstop: angled wing, with hood. Overall dimensions nominal 13 ft high x 20 ft wide x 6-1/2 ft deep.
11 68 23 | Exterior Court Athletic Equipment (Middle Schools) | Tennis Court Equipment: Porter/Gill Athletics; L.A. Steelcraft; Douglas Industries, Inc. | Removable tensioning crank.
11 68 23 | Exterior Court Athletic Equipment (High Schools) | Chinning Bar: Porter Athletic Equipment Co.; A.A.I.; Arizona Courtlines Outdoor Basketball: Jaypro; L.A. Steelcraft; Arizona Courtlines; First Team Tennis Court Equipment: Porter Athletic Equipment Co.; L.A. Steelcraft Products
11 68 33 | Athletic Field Equipment | Outdoor Basketball: L.A. Steelcraft; Arizona Courtlines; First Team Outdoor Volleyball: Porter; Arizona Courtlines Outdoor Athletic Bench at Dugouts: Miracle Recreation Equipment Co. #1267 Bike Racks: American Playground; Ultra Play Systems Trash Receptacle: Miracle Recreation Equipment Co.
Sports Edge: Pole Vault Boxes & Covers; Shot Put & Discus Circles; Shot Put Toe Boards; Pole LF/TJ Take Off Boards; Communication Boxes
Goal Posts: Porter Athletic Equipment Co. - Model 00296-232; A.D.P. – Lemco Pole Vault Liner and Cover: Gill Discus Cage and Netting: MF Athletic – Model 9976A Outdoor Athletic Bench at Dugouts: Miracle Recreation Equipment Co. #1267 Baseball Batting Cage Net: JUGS Softball Batting Cage Net: JUGS Bike Rack: American Playground – R-10; Ultra Play Systems - 5110 Trash Receptacle: Miracle Recreation Equipment Co. Powerhouse Batting Cages: Sports Edge Football Goals: Sports Edge Soccer Goals: Sports Edge
11 68 32 | Exterior Scoreboards | Football: Daktronics Model #FB-2019 size: 8' x 18'; Add "time-outs-left" on each side; team name in lieu of home; Nevco Model 7624 Fair-play Model #FB-8120TK-2 size: 7'-6" x 20'; team name in lieu of home; Soccer: Daktronics Model #SO-918 size: 4' x 12'; provide team name in lieu of home; Nevco Model 3602/3650 Fair-play Model #MP-8114-2 size: 4' x 14', team name in lieu of home; Baseball/Softball: Daktronics Model #BA-2017; size: 6' x 14' with Ball, Strike, Out, and "at Bat" showing numbers in lieu of dots; team name in lieu of home; Nevco Model 1610 Fair-play Model #BA-7200-2; xize: 5'-6" x 14' with Ball, Strike, Out and "at Bat" showing numbers in lieu of dots; team name in lieu of home. Controllers: provide one controller per school Daktronics Model "All Sport 5000"; Fair-Play Model MP-73. Include all related antenna and installation materials. Horn: Daktronics horn to be Model 55 trumpet - Fair-play - similar or standard horn. | Single Sided LED Scoreboards to be utilized for exterior locations. Provide 120V AC Controller with Radio Contol. Include hard side carrying case for controller Order sign backs that are dark colors. “RED” LEDs for outside use ONLY.
11 95 13 | Kiln | Basis of Design - Amaco Model No. EC-55 w/Master Vent Option; Electric; Ceramic; Top Load | Manufacturer's 5 year warranty required. 208 volt/single phase. Temperature range - 2019 degrees Fahrenheit max. Capacity - not less than 3.38 cu.ft.; approximate size: 18"W x 18"D x 18" H
12 | FURNISHINGS
12 21 13 | Horizontal Louver Blinds | Levelor Corporation; Kirsch; Blind Design | Vertical Blinds are to be utilized
12 21 16 | Vertical Louver Blinds | Manufacturers: Levelor (2-inch Dust Guard); Graber (G71 Superview; One Touch System); Blynco | Vertical Blinds are to be utilized. Include Headrail, tilter, wand, cord lock and all accessories for a complete installation.
12 32 00 | Manufacturered Plastic-Laminate-Clad Casework (Elementary & Secondary Schools) | Casework Manufacturers: Anderson; Caseworx, Inc.; Classy; Form-A-Fab; Granite Mill; LSI Corporation of America; Stevens Industries; TMI Systems Design; Corporation; Valley Custom Interiors, Inc.; Western Casework Plastic Laminate Manufacturers: Arborite Plus; Nevamar; Formica Corp.; Pionite; Wilsonart, Lamin-Art See Also section 06 40 00 Stainless Steel countertop: 14 gauge stainless steel unless shown otherwise, 1-1/2" dia. rolled edges, grind and polish all welds. | Basis of Design for quality & performance requirements: Trimline by TMI Systems; Storage systems are fully modular and dimensionally integrated to allow end user interchange of doors, drawer fronts, and interior components; products that do not have this standard feature/benefit will not be considered. AWI - American Woodwork Institute Compliance Required for All Casework. Provide Custom Grade Min.
12 35 53 12 36 53 | Laboratory Casework & Countertops (Secondary Schools) | Campbell Rhea/Mohon International; Caseworx Artisans; Hamilton Industries; Kewaunee Scientific Equip. Corp.; Diversified Woodcraft; Collegedale; Advanced Lab Concepts
12 48 43 | Floor Mats (Entry Mats) | Fluff-Cord Tile - R.C. Musson Rubber; Dura-Tile II - Pawling Corp.; Bretlin; Commercial | Type: Rubber fabric strip tiles.
12 61 00 | Fixed-Audience Seating | Irwin Seating Co.;Hussey; American Seating; Track Seating
12 63 00 | Stadium and Arena Bench Seating | Southern Bleacher; Schultz Industries – Sturdisteel; Reeves Steel, Inc.
12 92 13 | Bicycle & Scooter Racks | Bicycle Parking Racks: Madrax (Basis of Design GNS-8-IG-P) Powder Coated, hot dipped galvanized with Stainless Steel option, Scooter Rack - Velopa Kids Scooter Rack - Double Sided | Bicycle Rack - provide enough capacity for 24 bicycles loading from both sides.
13 | SPECIAL CONSTRUCTION
13 31 23 | Pre-Engineered Tensioned Fabric Structures | Tensioned Shade Structure Manufacturers: CCSD has a Unit Price contract with USA Shade for two sizes of fabric shade structures. 50' x 60' x 13'H is intended for cover primary and intermediate playground sets. 42' x 42' x 13'H fabric shade structures are intended to cover kindergarten playground sets. Fabric color shall be Royal blue. Steel color shall be Royal Blue. | Design the playground set so that the safety fall surface will provide 6' minimum clearance from the shade structure columns.
14 | CONVEYING EQUIPMENT
14 24 23 | Hydraulic Passenger Elevators | Manufacturers: Otis, Dover, Kone; Thyssen Krup | Holess Hydraulic Elevator
14 42 16 | Vertical Wheelchair Lifts | Concord, Garaventa; or other manufacturer as required to suit the specific jobsite conditions.
21 | FIRE SUPPRESSION
21 13 13 | Wet-Pipe Sprinkler Systems | Gate, Globe, Angle, Ball & Butterfly Valves: Apollo; Crane Co.; Grinnell Valves & Controls; Milwaukee Valve Co.; Mueller; Nibco Inc.; Shurjoint Piping Products, Inc.; Starfire, Inc.; Stockham, A Crane Company Check Valves: Crane Co.; Grinnell Valves & Controls; Milwaukee Valve Co.; Mueller; Nibco Inc.; Shurjoint Piping Products, Inc.; Stockham, A Crane Company; Victaulic, Reliable Drain Valves: Grinnell Valves & Controls; Nibco Inc.; Stockham, A Crane Company, United, Victaulic, FNW (Famillian North West) Sprinkler Heads: Tyco-Simplex-Grinnell; Reliable Automatic Sprinkler Co.; Viking Corp.; Victaulic Sprinkler Piping: Schedule 10 Steel Pipe CPVC Piping: CPVC fire sprinkler piping can be utilized in Light Hazard design occupancies when the manufacturer can provide test reports that demonstrate compliance with NFPA 13 Criteria, along with a UL Listing. CPVC Piping cannot be exposed to chemicals and must be stored per manufacturer's recommendations. | Fire Suppression Systems shall meet FM Global recommendations (including seismic bracing) and use components that are certified by FM Global wherever possible. CPVC experience and training: Experienced craftsmen with 5 years documented experience installing CPVC installations are required. Contractor to provide 40 hours of CPVC maintenance training for CCSD maintenance personnel. CPVC Piping Storage: Contractor to provide evidence of CPVC piping storage prior to use at the jobsite.
21 13 16 | Dry-Pipe Sprinkler Systems | Dry Pipe Valves: Reliable Automatic sprinkler Co., Viking, Tyco | (Do not utilize the Victaulic brand for dry valves. Expensive to repair, harder to troubleshoot.)
22 | PLUMBING
22 05 16 | Expansion Fittings and Loops for Plumbing Piping | Expansion Tanks: Armstrong; Dresser Inc./Wheatley; ITT Bell & Gossett; Taco; Amtrol
22 05 19 | Meters and Gages for Plumbing Piping | Domestic: Use Multiple 2" water meters. Grounds Water Meters: Small Elementary:(fields less than 80,000 sf) 100-110 gallons per minute, minimum of 2" water meters, multiple 2" meters acceptable. Regular Elementary (fields 80,000 to 180,000 sf) 240 gallons per minute, minimum of 3" turbine water meter. Middle School - 240 gallons per minute, minimum of 3" turbine water meter. High School - 500 gallons per minute, minimum of a 4" turbine water meter. | Separate Domestic and Irrigation Water Meters. Design Manual (Section N 1990's) Still Applicable. Alan Paulson (Operations & Grounds has history). George Jacoby - can utilize smaller irrigation meters, save first cost, eliminate constructing meter vault. Multiple 2" meters allow redundancy.
22 05 23 | General-Duty Valves for Plumbing Piping | General Valves: Apollo; Josam Co.; Jay R Smith Mfg. Co.; Precision Plumbing Products, Inc.; Zurn; Gate, Globe, Butterfly & Ball Valves: Anvil Gruvlok; Apollo; Crane Co.; Conbraco Industries; Hammond Valve; Kitz; Milwaukee Valve Co.; Nibco Inc.; Shurjoint Piping Products, Inc.; Stockham, A Crane Company Spring Loaded Check Valves: Apollo; Dresser Inc/Wheatley; Metraflex; Mueller Steam Specialty; Tyco Flow Control/Keystone Valves; Stratflo Products, Inc.; Val-Matic Valve & Mfg. Memory-Stop Circuit Balancing Valves: Apollo; Bell & Gossett; Flow Design, Inc.; Griswold Valve & Controls; Hammond Valve; Milwaukee Valve Co.; Nexus; Nibco; Taco, Inc.; Tour & Anderson Hydronics Thermostatic Water Mixing Valves: Apollo; Leonard Valve Co.; Symmons Industries, Inc.; Powers Models 431, 432, 433, 434, 1432 & 1434 Water Pressure Reducing & Relief Valves: Apollo; Bell & Gossett; Cash Acme; Watts Water Technologies, Inc.; Wilkins Operation; A Zurn Company Trap Seal Primer Valves & Systems: Josam Co.; Jay R Smith Mfg. Co.; Precision Plumbing Products, Inc.; Zurn Light | Provide Gate Valves for piping 6-inch diameter and above. Provide Butterfly Valves for piping 4-inch diameter and above. Provide Ball Valves for piping 3-inch diameter and less.
22 05 29 | Hangers and Supports for Plumbing Piping and Equipment | Fixture Supports: Jay R. Smith Mfg.; Zurn; Josam; Construction Engineered Attachment Solutions
22 05 33 | Heat Tracing for Plumbing Piping
22 05 48 | Vibration and Seismic Controls for Plumbing Piping and Equipment
22 05 76 | Facility Drainage Piping Cleanouts
22 07 00 | Plumbing Insulation | Pre-insulated Pipe Assembly: Thermacor Process, LP; Thermal Pipe Systems, Inc.; Ric-Will Piping Systems, Perma-Pipe, Inc.
22 11 00 | Facility Water Distribution
22 10 00 | Plumbing Piping | Incomming Underground Main Service Piping: HDPE is allowed for exterior above grade and below grade areas. C900 & PVC Piping are also allowed. | HDPE experience & Training: Experienced craftsmen with 5 years documented HDPE installation experience is required. Contractor to provide 40 hours of HDPE pipe maintenance training for CCSD maintenance personnel.
22 11 16 | Domestic Water Piping | Water Hammer Arresters: Jay R. Smith Mfg. Co.; Josam Company; Zurn Specification, Drainage Operation Backflow Preventers: Febco; Watts Water Technologies, Inc.; Wilkins Operation (A Zurn Company) Hose Bibbs and Wall Hydrants: American Standard, Moen, Chicago Faucet; Wade; Woodford Manufacturing Co. Woodford Manufacturing Co. is preferred with frost free Wall Hydrant Design. Plumbing Outlet Boxes: see Hose Bibbs above Domestic Water Piping: Piping, Domestic: Utilize copper piping for main branch piping. PEX is allowed for 2" and smaller than pipe. PVC piping is allowed for domestic water piping. | PEX experience and training: Experienced craftsmen with 5 years documented experience using PEX installations are required. Pex Crimp connections and other installation requirements must meet manufacturer's pre-printed installation instructions. Contractor to provide 40 hours of PEX maintenance training for CCSD maintenance personnel.
22 11 23 | Domestic Water Pumps | In-Line Circulator Pumps: Armstrong Pumps, Inc.; Bell & Gossett; Grunfoss
22 13 00 | Facility Sanitary Sewerage | HDPE piping is allowed for exterior sewer piping below building. SDR35 Sewer piping is also allowed. | See additional experience and training requirements in section 22 10 00
22 13 16 | Sanitary Waste and Vent Piping | Piping, Non-Domestic: Utilize PVC in wall or chase construction; Utilize CPVC in Plenum Rated Locations. Minimum Schedule 40 is required for both PVC & CPVC. CPVC Manufacturer with current ICC ES Report showing compliance with ASTM E-84: Spears Manufacturing, Inc. EverTuff SDR 11 and EverTuff Industrial CPVC; 1/2"dia. up to 6" dia. pipe size. CPVC Piping cannot be exposed to chemicals and must be stored per manufacturer's recommendations. | CPVC Piping: Manufacturers of Plenum Rated CPVC Products must submit testing & compliance with ASTM E84 Smoke & Flame requirements prior to installation. Engineer to Utilize appropriate plastic valves when designing PVC & CPVC Systems. CPVC experience & Training: Experienced craftsmen with 5 years documented CPVC installation experience is required. Contractor to provide 40 hours of CPVC maintenance training for CCSD maintenance personnel. CPVC Piping Storage: Contractor to provide evidence of CPVC piping storage prior to use at the jobsite.
22 13 19 | Sanitary Waste Piping Specialties | Floor Drainage / Floor Sinks: Jay R Smith Mfg. Co.; Josam Co.; Cleanouts: Jay R. Smith Mfg. Co.; Josam Company; Zurn Specification Drainage Operation Trap Guards: Trap Guards are to be used in lieu of Trap Primers. For Trap Guard Products provide manufacturer's standard 10 year warranty.
22 33 00 22 34 00 22 35 00 | Domestic Water Heaters (Electric & Fuel-Fired); Domestic Water Heat Exchangers | Water Heaters: Bradford White Corporation; Lochinvar; RBI Mestek; Rheem Mfg. Co.; A O Smith Water Products Co.; WaterHeater Cement Lined Water Storage Tanks: Hubbel - Model E, SE only | Cement lined water storage tanks only to be considered if budget allows the higher initial costs.
22 40 00 | Plumbing Fixtures
22 42 00 | Commercial Plumbing Fixtures
22 42 13 | Commercial Water Closets, Urinals, and Bidets | Water Closets: Wall Mount Top Spud (Preferred for New Construction): Amer. Standard Afwall Model 2257.103; Toto Model CT 708; Kohler Model Kingston K-4330 Floor Mount Top Spud: Amer. Standard Madera Model 2234.015; Toto Model CT 705; Kohler Model Wellcomme K-4350 Wall Mount Back Spud (To be used for Modernization Projects ONLY to match existing plumbing arrangement): Amer. Standard Afwall Model 2257.103; Toto Model CT 708V; Kohler Model Kingston K-4330 Urinals: Top Spud Inlet (Preferred for New Construction): Amer. Standard Washbrook Model 6501.010; Toto Model UT 477; Kohler Model Bardon Superior K-4960-ET Urinals, Waterless: Waterless Sierra Model 2102; Sloan Waterfree Model WES-1000; Zurn Sahara Model Z5795 Back Spud Inlet (To be used for Modernization Projects ONLY to match existing plumbing arrangement): Amer. Standard Washbrook Model 6506.011; Toto Model UT 447V; Kohler Model Dexter K-5016-ER | New construction shall not utilize chaseway designs or flushometers; or sensors in student toilet rooms.
22 42 16 | Commercial Lavatories and Sinks | Lavatories: Lavatories: American Standard; Briggs Industries; Gerber; Kohler; Willoughby Lavatory Fittings - Single Push Handle Mixing Faucet: Basis of Design: T & S Brass Model B-0712-VF05-4DP/5EF-006 - Mixing Valve Basis of Design - WATTS - Series -LFUSG-B Under Sink Guardian - Lead Free Non-Mixing Faucet: Chicago Model 802-V665CP; Kohler Model K15636-CP; Zurn Model Z-86500 Gooseneck Faucet: Chicago Model 350-CP; Elkay Model LK 20858 Sinks: Sinks: Advance Tabco; Elkay Manufacturing; Moen, Inc. Sink Fittings - Wall Mount Kitchen Sink Faucets: Chicago Model 445-CP, single swing; Chicago Model 455-DJ18-CP, double swing; Elkay Model LK-67C, 13” reach; Elkay Model LK-67DDJ18, double swing Deck Mount Science Sink Faucet: Chicago Model 928-CP, with AVB Service Sinks: American Standard Lakewell Model 7692.049; Eljer Rollins Model 242-0135 Service Sink – Floor Mounted: American Standard Florwell Model 7740.020; Stern Williams Model HL-1800; Stern Williams Model CRS-2200 Service Sink Fittings - Wall-Mount Service Sink Faucets (with stops - required): Chicago Model 305 VBRCF; Chicago Model 897-RCF with hook; Elkay Model LK-400; Elkay Model LK410B; Kohler Model K-8905-RP; Kohler Model K-8906-RP
22 42 23 | Commercial Showers | Individual Showers: Florestone Products Co.; HydroSystems; LASCO Bathware Locker Room Shower Fittings: Powers Hydroguard T/P
22 42 33 | Wash Fountains | Wash Fountains - Semi-Circle: Acorn Model 3544-H-BO-CS; Bradley Model SN2004/AST; Willoughby Model WWF-3604-PMI Wash Fountain - Circular: Acorn Model 3508-H-BO-CS; Bradley Model SN2008/AST; Willoughby Model WWF-5408-PMI | Wash Fountains are not to be used. Provide individual lavoratories only, see section 22 42 16 above.
22 42 43 | Flushometers | Flushometers – Water Closet: Sloan Royal Model 111; Zurn Aquaflush Model Z6000-WS1 Flushometers – Urinal: Sloan Royal Model 180-1.0 ; Zurn Aquaflush Model Z6001-WS1 | Flushometers shall only be used for administrative facilities and not for student toilet rooms.
22 45 26 | Eye/Face Wash Equipment | Guardian; Haws; Speakman | Haws is the preferred Manufacturer
22 47 00 | Drinking Fountains and Water Coolers | Drinking Fountains: Elkay; Haws; Sunroc Electric Water Coolers (EWC): Elkay; Halsey Taylor; Sunroc; Haws | EWC: Elkay Preferred
22 66 83 | Chemical-Waste Tanks | Acid Waste System including neutralization tanks: Orion Fittings, Inc.; Zurn Chemical Drainage Group; Enfield
23 | Heating Ventilating & Air Conditioning (HVAC)
23 05 14 | Variable-Frequency Motor Controllers | Danfoss Graham, Div. Of Danfoss, Inc., ABB, Square D, Yaskawa | Variable Frequency Controllers: Three-Phase variable frequency motor controllers for fan and pump motors.
23 05 16 | Expansion Fittings and Loops for HVAC Piping | Adsco Manufacturing LLC, Amber/Booth Company, Inc., Flex-Weld, Inc/Keflex, Hyspan Precision Products, Inc., Mason Industries, Inc./Mercer Rubber Co., Metraflex Co., Proco Products, Inc., Senior Flexonics, Inc., Unaflex Incorporated | Fittings for thermal expansion and movement compensation in piping systems for fire protection, plumbing, hydronic, steam, and refrigerant systems.
23 05 19 | Meters and Gages for HVAC Piping | Alnor Instrument Co., Bristol Babcock, Dwyer Cali-Tech, Marsh Bellofram, Precision Control Div., Miljoco, Palmer, Taylor, Weiss, Weksler | Fixed measuring devices and specialty items for hydronic, steam and steam condensate piping system.
23 05 23 | General-Duty Valves for HVAC Piping | Gate Valve, Plug Valves, Butterfly, Ball | lvt
23 05 29 | Hangers and Supports for HVAC Piping and Equipment | Thermo Hanger Shield, Inc., Portable Pipe, Hanger, Inc., Channel Support Systems, Miro Industries, Construction Engineered Attachment Solutions
23 05 33 | Heat Tracing for HVAC Piping | Thermon, Chromalox, Raychem
23 05 48 | Vibration and Seismic Controls for HVAC Piping and Equipment | Amber/Booth Company, Inc., I.S.A.T. (International Seismic Application Technology), Kinetic Noise Control, Inc., Mason Industries, Inc., M W Sausse/Vibrex
23 05 53 | Identification for HVAC Piping and Equipment | Brady Corporation, Brimar Industries, Inc., Marking Services, Inc. (MSI), Panduit Corporation, Seton Identification Products
23 07 13 | Duct Insulation | Duct, Pipe & Equipment Insulation: CertainTeed Corporation, Johns Manville Corporation, Knauf Fiber Glass, Manson Insulation, Inc., Owens Corning | Thermal and acoustic insulation for ductwork and air handling devices, equipment, and piping systems
23 08 00 | Commissioning of HVAC
23 09 00 | Instrumentation and Control for HVAC
23 09 13 | Instrumentation and Control for HVAC | Multi-System Integration Platform (MSIP): Tridium | USE BUILDING AUTOMATION SYSTEM FOR CONTROLS.
23 09 13 | Actuators and Operators
23 09 13 | Sensors and Transmitters
23 09 13 | Control Valves | Control Valves, Assemblies: Belimo – (2” and under), Bray Controls (2 ½” and larger), Honeywell, Johnson, Siemens
23 0913 | Shut off Valves | Belimo, Bray, Keystone
23 09 13 | Control Dampers
23 09 23 | Direct-Digital Control System for HVAC | Alerton (BacTalk), Automated Logic (Web Control), Delta (OrcaView), Schneider (Intelligent Automation) | Components and software for a direct digital control system.
23 09 33 | Electric and Electronic Control System for HVAC | Damper Actuators, Electronic: Belimo, Honeywell, Siemens
23 09 43 | Pneumatic Control System for HVAC | Pneumatic System Providers: Invensys, Honeywell, Johnson Controls, Siemens Building Technologies Damper Actuators, Pneumatic: Bray Controls, Honeywell, Johnson, Siemens
23 11 00 | HVAC - FACILITY FUEL PIPING
23 11 23 | Facility Natural-Gas Piping | ASTM A53 Metallic Gas Pipe: Wheatland Tube, Valencia Pipe Company, SAHA Thai Steel Public Co. Ltd. | Per 2012 UPC Section 301, all Metallic Gas Pipe and Fuel Gas Pipe Fittings in a gas piping system shall be listed by an approved Listing Agnecy to the appropriate Standard - IAPMO, UL, ICC-ES
Fuel Gas Pipe Fittings: SCI (Smith Cooper); Viega LLC - Press-connect metalic fittings; BIS Pipe; Jinan; Charman Manufacturing - Malleable Threaded Fittings classes 150 and 300;
23 21 23 | Base-Mounted, Centrifugal Hydronic Pumps | Packaged Pumping Systems: Syncroflo, Systecon | Not Recommended
23 20 00 | HVAC PIPING and PUMPS
23 21 00 | Hyrdonic Piping and Pumps
23 21 23 | Hydronic Pumps | Pumps: Armstrong Pumps, Inc., Aurora Pump, ITT/Bell & Gossett , Paco Pumps, Taco Inc., Weinman, A Crane Company | Centrifugal pumps and accessories for hydronic systems and condensate and boiler feed pumps for steam systems.
Pump Motors: US Motors, Baldor, Armstrong
23 21 23 | Base-Mounted, Centrifugal Hydronic Pumps | Packaged Pumping Systems: Syncroflo, Systecon | Not Recommended
23 22 00 | Steam and Condensate Piping and Pumps | CCSD is not using Steam Systems
23 23 00 | Refrigerant Piping
23 23 13 | Refrigerant Piping Valves | Refrigerant Valves: Danfoss Electronic Inc., Henry Valve Co., Sporlan Valve Co., ASCO Valve Co.
23 23 16 | Refrigerant Piping Specialties
23 23 19 | Refrigerant Safety Relief Valve Dishcarge Piping | Safety Valves: Amtrol Inc., ITT McDonnell & Miller, Tyco/Kunkle Valve Division, Watts Water Technologies, Inc.
23 23 23 | Refrigerants | R134a only; JFC-410A, 507, R22, 407C | Revisit Decision October 2016
23 24 00 | Internal-Combustion Engine Piping
23 25 00 | HVAC Water Treatment | Chemical Water Treatment: ChemAqua, Inc., Solution Metering Pump: LMI/Milton Roy, Company Mueller/Walchem | Provide a Peristaltic Type of Pump - any brand
23 25 13 | Water Treatment for Closed-Loop Hydronic Systems | See 23 25 00
23 25 16 | Water Treatment for Open Hydronic Systems | See 23 25 00
Chemical Feeder: Lakewood Controller
23 30 00 | HVAC AIR DISTRUBUTION
23 31 00 | HVAC Ducts & Casings | Single Wall Round Ducts: ASI, SEMCO, United McGill Grooved Mechanical Joint Fittings and Couplings: Anvil Gruvlok, Grinnell, Shurjoint Piping Products, Inc., Victaulic Company
23 33 13 | Dampers | Fire & Combination Fire/Smoke Dampers: Nailor Industires, Pottorff, Ruskin, Safe-Air Dowco Backdraft Dampers: Acme, Cesco, Dowco, Penn, Ruskin, Safe Air
23 33 33 | Duct-Mounting Access Doors | Bilco, Ductmate, Elmdor, Milcor, Nailor Industries
23 34 00 | HVAC Fans | Cabinet & Ceiling Exhaust Fans: Breidert, Carnes, Cook, Greenheck, Penn, Twin City Fan
23 34 13 | Axial HVAC Fans
23 34 16 | Centrifugal HVAC Fans
23 34 23 | HVAC Power Ventilators | Roof Exhausters: Acme, Cook, Greenheck, Penn
23 34 33 | Air Curtains | Mars, Inc., Twin City Fan
23 35 00 | Special Exhaust Systems
23 35 13 | Dust Collection Systems | Sawdust Collection Systems: Torrit
23 35 16 | Engine Exhaust Systems |  | Maintenance to find out what product we are utilizing
23 36 00 | Air Terminal Units | Carnes, Envirotec, Kreuger, Metalaire Inc., Titus ESV | Constant and variable volume terminal units for duct systems including dampers, hardware, and controls.
23 37 00 | Air Outlets and Inlets | Diffusers, Registers, and Grilles: Anemostat, Carnes Co., Krueger, Metal-Aire, Nailor Industries, Price Industries, Titus, Tuttle & Bailey Louvers: American Warming Ventilating, Cesco Products, Greenheck, Industrial Louvers, Inc., Ruskin Co., Safe-Air/Dowco
23 40 00 | HVAC AIR CLEANING DEVICES
23 41 00 | Particulate Air Filtration | Cambridge, Eco Air, Farr, StrionAir System
23 50 00 | CENTRAL HEATING EQUIPMENT
23 51 00 | Breechings, Chimneys, and Stacks | Breechings, Chimneys and Stacks: American Metal Products Co., Metal-Fab, Inc., Selkirk Metalbestos
23 52 00 | Heating Boilers
23 52 16 | Condensing Boilers | For use in systems designed to take advantage of their energy savings ability
23 52 23 | Cast-Iron Boilers | Hydro Therm
23 52 33 | Water-Tube Boilers | Finned Water-Tube Boilers: (Non-Condensing Type) Camus, Kewanee, Laars, Lochinvar, Raypak, RBI Mestek, Thermal Solutions, ACE Heater -Triton series
23 53 00 | Heating Boiler Feedwater Equipment
23 57 00 | Heat Exchangers for HVAC | Alfa Laval, Armstrong, Bell and Gossett, Mueller, Tranter
23 60 00 | CENTRAL COOLING EQUIPMENT
23 64 00 | Packaged Water Chillers
| Air-Cooled Chillers | Carrier, Daikin, McQuay, Trane, JCI (York), Smardt
| Water-Cooled Chillers | Arctic Cool, Carrier, Daikin, McQuay, MultiStack, Smardt, Trane, York | Water cooled chillers shall be oil free, magnetic bearing type. In projects where only one chiller is being installed, the chiller shall include at least two compressors. If two or more chillers are to be installed on a project, the chillers may include a single or multiple compressor configuration.
23 65 00 | Cooling Towers | Cooling Towers: LTSA-Reymsa Cooling Towers, Baltimore Air Coil (BAC), Marley, Evapco towers to be cross flow. Cooling Tower Filter System: Griswold, Lakos, Puro Flux Cooling Tower Level Control: Mechanical float switch. | CCSD has changed from counterflow cooling towers to crossflow, due to their ease of maintenance as compared to the counterflow cooling towers. Revised - CCSD will allow counterflow and cross flow cooling towers.
23 70 00 | CENTRAL HVAC EQUIPMENT
23 72 00 | Air-to-Air Energy Recovery Equipment | Energy Recovery Units: Carrier, Des Champs Technologies, Greenheck, Innergey Tech, Inc.
23 74 00 | Packaged Outdoor HVAC Equipment | Air Handling Units: Energy Labs Inc., Governaire Corporation, Huntair, Mammoth Inc., Scott Springfield Mfg. Inc., Temtrol Inc., Alliance Air Products, Annexair, Daikin Packaged Rooftop Air Conditioning Units (Self Contained): Carrier, Governaire Corporation, Lennox, Mammoth Inc., Trane, York, Alliance Air Products. Seasons-4, Annexair, Daikin, Tempmaster | CCSD strongly prefers the units to be controlled by the building automation system in lieu of proprietary 3rd party controls.
23 74 13 | Multizone Packaged Outdoor Central Station Air Handling Units | Air Handling Units: Alliance; Energy Labs Inc.; Governaire Corporation; Huntair; Mammoth Inc.; Scott Springfield Mfg. Inc.; Temtrol Inc.; Seasons-4; Unitech, Annexair, Miller Picking/Pace | CCSD strongly prefers the units to be controlled by the building automation system in lieu of proprietary 3rd party controls. Please also see section 23 81 46 Water Source Heat Pumps
23 75 00 | Custom-Packaged Outdoor HVAC Equipment | Packaged Central Plant Inc., Aaon Inc., Armstrong, Chil-Pak, Governaire Corporation, Systecon, Mammoth, Inc. (must be manufactured at Springfield MO facility)* | DO NOT USE
23 76 00 | Direct Evaporative Air-Cooling Equipment | Ares, Arvin, Champion Cooler Corporation, Essick Air Products | Do not use Indirect Evaporative Air Coolers
23 80 00 | DECENTRALIZED HVAC EQUIPMENT
23 81 00 | Decentralized Unitary HVAC Equipment
23 81 13 | Packaged Terminal Air-Conditioners | Envirotec, International, Modine, Reznor
23 81 26 | Split-System Air-Conditioners | Carrier , Mitsubishi, Sanyo, Lennox | Units consisting of air handling unit and condensing unit with electric cooling: electric or hot water heating and controls.
23 81 29 | Variable Refrigerant Flow HVAC Systems
23 81 00 | Decentralized Unitary HVAC Equipment | Unitary Heat Pumps (Air): Carrier, Lennox, Mammoth, Trane, York | Roof mounted self-contained heat pumps, packaged free standing or through-the-wall terminal heat pump units, and packaged heat pump units with remote condensers.
23 81 46 | Water Source Unitary Heat Pumps (WSHP) | Approved Vendors: ClimateMaster: Vertical Stack Water Source Heat Pump, removable chassis (TSL) “Tranquility”, motorized on/off valve to be disabled/removed per special requirements. Provide shut off valves at coil connections on chassis. Factory to install rubber bushings on supply and return pipes where clamped to air coil. Daikin Vertical Stack Water Source Heat Pump, Model VHF Cabinet and VHC/VHW Chassis, motorized on/off valve to be disabled/removed per special requirements. AE Air - Model HRCC: Removable chassis, motorized on/off valve to be disabled/removed per special requirements. Whalen Series VI Water Source Heat Pump and Air Conditioner, motorized on/off valve to be disabled/removed per special requirements. Zehnder Rittling, Vertical Stack Series Water Source Heat Pump, Model VHN motorized on/off valve to be disabled/removed per special requirements. | WSHP - Special Requirements for New Schools: To be installed in a closet next to the room (classroom or other) with a door to the corridor. Said room to enclose the heat pump equipment including supply and return risers, and serve as a plenum. Water source heat pump, cabinet and chassis are to be located within the plenum. Also, within the plenum, but outside the water source cabinet, on the right side close to the front is to be located the supply and return risers. A full sized bypass (similar to Nexus BKUC) shall be provided above supply and return riser shut-off valves and strainers to allow for flushing of the system. The motorized on/off control valve on the chassis of the water source heat pump is to be replaced by a motorized Belimo on/off, normally closed control valve relocated external to the water source cabinet in the plenum on the return riser. Actuator is to be provided with electrical whip and plug. Actuator to be plugged in by startup technician after the main system has been flushed and cleaned. Condensate pumps are to be provided in the plenum for units on the first floor and piped to the adjacent sink in classroom. Second floor unit condensate shall drain by gravity to sink on first floor. Chassis when installed must be at least 9” above finished floor. Door to the plenum must be sealed to prevent air leaks.
23 82 00 | Convection Heating and Cooling Units
23 82 19 | Fan Coil Units | See Section 23 74 13
23 84 00 | Humidity Control Equipment
25 | INTEGRATED AUTOMATION
25 00 00 | Integrated Automation | Approved Manufacturers: Alerton Automated Logic Delta Distech Schneider Electric (CCSD will consider other manufacturers in cases where the existing building automation system is proprietary and compatibility is an issue) | BACNET Communications Hardware & Software Platform Only, with the following additional requirements: - Installer shall have min. 5 years documented experience installing manufacturer's DDC controls. - Installer main office to be within 60 mile radius of project site location. See Division 25 specifications for additional installer qualifications. LONMARK Hardware & Software is not acceptable Multi-System Integration Platform (MSIP): Tridium required for HVAC Systems USE BUILDING AUTOMATION SYSTEM FOR CONTROLS.
26 | ELECTRICAL
26 01 00 | Operation & Maintenance of Electrical Systems
26 05 00 | Common Work Results for Electrical
26 05 19 | Low-Voltage Electrical Power Cables | Connectors & Splices: AFC Cable Systems Inc., Hubble EGS Electrical Group (Appleton, McGill, Easy Heat, OZ/Gedney, Tyco Electronics Corp.
Sleeve Seals: Advance Products & Systems Inc., Calpico Inc., Metraflex Co, Pipline Seal & Insulator Inc., Thomas & Betts.
26 09 19 | Contactors | Square D, General Electric, Siemens, Allen, Bradley, ASCO
26 05 26 | Grounding & Bonding for Electrical Power Cables | Exothermic Connection: Cadwell by Enrico, 3M Elect. Products
26 05 29 | Hangars & Supports for Electrical Systems | Steel Channel: Unistrut, Channel Support Systems, Construction Engineered Attachment Solutions
26 05 33 | Raceway & Boxes for Electrical Systems | Metal Wireways: Cooper; B-Line Inc.; Hoffman; Square D; Thomas & Betts Non-Metal Wireways: Lamson & Sessions; Carleson Electric Products; Thomas & Betts Surface Metal Raceways: Thomas & Betts Corp; Walker Systems Inc.; Wiremold Co. (Elect.SalesDiv.) Wiremold:Model V500 for extension to individual outlets only, Model V700 for data & ITV outlets, Model V4000 for other applications, Mono Systems is an acceptable alternate for the V4000, Thomas & Betts MC Cable: is acceptable for use in raceway locations except where it is visible to the public (i.e. where the ceiling is open to the structure). Recessed Gang Floor Boxes: Hubbel SystemOne 4 Gang - CFB4G25 and 10 Gang - CFB10G55 for use in concrete flooring USB Charging Duplex Receptacle: Hubbel USB20A5
26 05 36 | Cable Trays for Electrical Systems | MP Husky; Chalfant; Eaton (B-Line); Monosystems
26 05 39 | Underfloor Raceways for Electrical Systems (Walker Duct) |  | Prefer not to use Underfloor Raceways
26 05 43 | Underground Ducts & Raceways for Electrical Systems | PVC Conduit | Prefer not to use Underfloor Raceways
26 05 53 | Identification for Electrical Sytems | 3M Elect. Products, Brady, Thomas & Betts Corp.
26 05 73 | Overcurrent Protective Device Coordination Study | Include the following in the electrical scope of work: A/E teams to specify that the Contractor provide a preliminary Short Circuit Analysis with Calculations, an NFPA 70E Arc-Flash Analysis with proper PPE & labeling requirements, and a Coordination Study to assure the protective device closest to a fault trips first and to establish the proper interrupting ratings of protective devices (based on approximate distances). This report shall be submitted with the switchgear, switchboard, and panelboard submittals. Later, when final distances are available, the Contractor shall provide minor modifications with the final analysis and final proposed labeling at least 20 days prior to the labeling installation. All reports are to be provided to the Owner and the Engineer of record for review and comment.
26 05 43 | Underground Ducts and Raceways for Electrical Systems | PVC Conduit is acceptable for use underground
26 05 26 | Grounding and Bonding for Electrical Systems | Rods used for Electrical Grounding or Earthing: provide 1" diameter x 10-foot long Stainless Steel Grounding Rods in lieu of 1" dia. X 8-foot long Steel Copper Clad Grounding Rods. | For new construction use stainless steel grounding rods only if the 5 Ohm resistence requirement cannot be met with the concrete encased electrode (UFER ground). For Building Additions and/or Portable Classroom Installations - provide Stainless Steel Grounding Rods. Over time a safety issue occurs when the copper cladding corrodes from contact with corrosive soils or becomes dented in rocky soils.
26 05 83 | Wiring Connections | 3M Elect. Products, Hubbell, Thomas & Betts Corp.
26 06 00 | Schedules for Electrical
26 08 00 | Commissioning of Electrical Systems | by CCSD Energy Management Dept
26 09 00 | Instrumentation & Control for Electrical Systems
26 09 13 | Electrical Power Monitoring & Control
26 09 19 | Enclosed Contactors | Square D, General Electric, Siemens, Allen, Bradley, ASCO
26 09 23 | Lighting Control Devices | LED Lighting Control Systems for New Construction: Approved System manufacturer's include: "Greengate", "Douglas Lighting Controls" and "Synergy". Lighting Control shall be on a classroom by classroom basis with automatic connection to both Occupancy Sensors and Daylighting Sensors (as applicable to the room). Non LED Occupancy Sensors: Hubbell, Sensor Switch, Wattstopper LED Occupancy Sensors - Auto on/Auto off, (Dual) Occupancy (Motion Activated): Hubbell, Sensor Switch, Wallstopper, or as required for LED lighting control system. Daylight Sensors: as required for lighting control system. | NEW CONSTRUCTION: Teacher LED Classroom controls 6 stations: on-full to meet Health District Requirements per below; up/down (adjustable to 10%), off, AV, and quiet time setting that over-rides the function for a period of time. Locate control by classroom entry door. Classroom LED Control: on/off control at the entry door. LED Lighting at Teacher Station: IES NA Light Levels: Refer to RP-3-00, Table 1 & 2 useas Minimum Levels. June 12, 2012 Health Dept.Letter to CCSD also applies: IESNA Lighting Handbook and IESNA RP-6 Recommended Practice for Sports and Recreational Area Lighting.
26 09 26 | Lighting Control Panelboards
26 09 33 | Central Dimming Controls | Not Used, prefer controls on a classroom by classroom basis per 26 09 23 above.
26 09 61 | Theatrical Lighting Controls
26 10 00 | Medium Voltage Electrical Distribution
26 11 00 | Substations
26 12 00 | Medium-Voltage Transformers | General Electric, Square D, Siemens, Acme, Powersmiths, PQI (Power Quality International) | "K" rated or Harmonically Mitigated. Isolated Ground and Isolated Neutral
26 13 00 | Medium-Voltage Switchgear
26 18 00 | Medium-Voltage Circuit Protection Devices
26 20 00 | LOW-VOLTAGE ELECTRICAL DISTRIBUTION
26 22 13 | Low-Voltage, Energy Efficient, Dry -type,Distribution Transformers | General Electric, Square D, Siemens, Acme, Powersmiths, Hammon, PQI (Power Quality International) Eaton | Must comply with DOE 2016 amended energy efficiency standards to 10 CFR Part 431 "Energy Conservation Program: Energy Conservation Standards for Distribution Transformers, Final Rule" dated April 18, 2013.
26 24 00 | Switchboards and Panelboards | Aluminum feeders from main switchgear/switchboard to panels are allowed. Compression terminals approved for aluminum conductors are required. | Installer shall have 5 years documented experience installing and terminating aluminum feeders. CCSD building inspector shall be present to observe the terminations.
26 24 13 | Switchboards | Square D, General Electric, Siemens
26 24 16 | Panelboards | Square D, General Electric, Siemens, Cutler-Hammer
26 24 19 | Motor-Control Centers | Siemens, Square D, GE
26 27 00 | Low-Voltage Distribution Equipment
| Cords & Caps | Woodhead, Hubbell, Leviton, Pass & Seymour
26 27 26 | Wiring Devices (Switches & Receptacles) | Leviton; Pass & Seymour; Hubbell; Cooper; Woodhead; General Electric
26 28 00 | Low-Voltage Circuit Protective Devices | Siemens, Square D, GE
| Fuses | Cooper Bussman Mfg. Co.; Ferraz Shawmut; Little Fuse | (Note: Challenger equipment not acceptable)
| Moulded Case Circuit Breakers | Square D; General Electric; Siemens | (Note: Challenger equipment not acceptable)
| Enclosed Switches & Circuit Breakers | Square D Co.; General Electric Co.; Siemens | (Note: Challenger equipment not acceptable)
26 29 00 | Disconnect Switches & Over current Protective Devices
| Low-Voltage Enclosed Controllers | Square D, General Electric, Allen-Bradley, Siemens | All Controllers shall be enclosed
Disconnect Switches
26 30 00 | FACILITY ELECTRICAL POWER GENERATING & STORING EQUIPMENT
26 31 00 | Photovoltaic Collectors
26 32 00 | Packaged Generator Assemblies
26 32 13 | Engine Generators (Diesel-Engine Driven) | Kohler, Generac, Commins Onan, Caterpillar
26 32 36 | Restive Load Banks |  | Revisit Section November 2015
26 33 00 | Battery Equipment
26 33 53 | Static Uninterruptible Power Supply | APC
26 35 00 | Power Filters & Conditioners
26 36 00 | Transfer Switches
26 36 13 | Manual Transfer Switches |  | Use Automatic Only
26 36 23 | Automatic Transfer Switches | Kohler, Detroit Diesel Spectrum, ASCO, Commins Onan, Genco Generac
26 40 00 | ELECTRICAL & CATHODIC PROTECTION
26 41 00 | Facility Lightning Protection
26 41 23 | Lightening Protection Surge Arressters and Suppressors | Square D | Revisit
26 43 00 | Surge Protective Devices
26 43 13 | Surge Protection Devices for Low-Voltage Electrical Power Circuits |  | Revisit
26 50 00 | LIGHTING
26 51 00 | Interior Lighting | Classroom Lighting Design (New Construction): Use LED Fixtures. Follow CHPS California Lighting Standards for classroom layout. Provide controls by the teacher station. Space remaining LED Classroom lights to meet CCSD Health District Light Levels (See Section 26 09 23). Provide a light above classroom entry from the hall tied to the emergency lighting system. | This control system has a built in approved automatic transfer switch for egress lighting. Using that control, the classroom egress lighting (light by the door) would not come on when the alarm is triggered. The classrooms will stay dark unless the perpetrator entered at which time all the classroom lights would come on. In the case of a power failure the light above the door would be automatically transferred to the emergency circuit and provide the required egress lighting. "LED Light Fixtures must have serviceable Diode's and Drivers without removal of the fixture."
26 51 13 | Interior Lighting Fixtures, Lamps, & Ballasts
| Lamps (Fluorescent) | Sylvania/Osram, General Electric, Philips, Venture | Fluorescent fixtures used if required to match existing systems. New Construction shall use LED Fixtures.
| Ballasts (Fluorescent) | Advance, Optanium Instant Start | Fluorescent fixtures used if required to match existing systems. New Construction shall use LED Fixtures.
| Luminaires (Fluorescent Fixtures) | Cooper, General Electric, H.E. Williams, Holophane, Hubbell, Kenall, Kim, Lithonia, Luminaire, Nulite, Prescolite | Fluorescent fixtures used if required to match existing systems. New Construction shall use LED Fixtures.
Reference No. | LED | New Construction shall be provided with LED Lighting: LED Lighting Packages are being developed as part of several new prototype schools. Approved Fixtures are as follows: | Driver and LED Modules within LED fixtures shall be field serviceable, without removable of the fixture, unless fixture replacement is required for the Diode. Fixtures are designed for 4,000 Kelvin All LED Fixtures shall have a 5-year warranty minimum.
| 2' X 4' LED | LITHONIA - 2GTL4
F1 | TROFFER | METALUX - 24GR | Equipment Room and Telecommunications Room
| 82 Watts max | COLUMBIA - LJT24
| LPW 121 min | H. E. WILLIAMS LPT-24
| 4000K | LA LIGHTING - 2-GHL320
| CRI 80+ / 0-10V DIMMING | LSI Midwest Lighting GA24
MOBERN RG Series Troffers
| 2' X 4' LED | LITHONIA - 2GTL4
F2 | TROFFER | METALUX - 24GR | Office Locations
| 45 Watt max | COLUMBIA - LJT24
| LPW 121 min | H. E. WILLIAMS LPT
| 4000K | LA LIGHTING - 2-GHL320
| CRI 80+ / 0-10V DIMMING | LSI Midwest Lighting GA24-LED
MOBERN RG Series Troffers
| 2' X 4' LED | LITHONIA-2GTL4 48L EZ1 LP840
F3 | TROFFER | METALUX - 24GR-LD4-48-F1-UNV-L840-CD-U | Corridors and Office Locations
| 43 Watt | COLUMBIA - LJT24-40MLG-FSA12125-EDU-PAF
H. E. WILLIAMS LPT-24-L67/840-SA12125-(L4800)-DIM-UNV
LA LIGHTING - 2-GHL320-6K-HE-4L-FSW-FPA-FPA2-1DRDM-UNV-2-840
MOBERN RG Series Troffers
LSI Midwest Lighting GA24-LED-SS-NW-UE-P12
| 2' X 4' LED | LITHONIA-2GTL4
F3 | TROFFER | METALUX - 24GR-LD4 | Corridors and Office Locations
| 46 Watt max | COLUMBIA - LJT24
| LPW 121 min | H. E. WILLIAMS LPT-24
| 4000K | LA LIGHTING GHL320
| CRI 80+ / 0-10V DIMMING | MOBERN RG Series Troffers
LSI Midwest Lighting GA24
| 1'X4' LED | LITHONIA-GTL4
F4 | RECESSED TROFFER | METALUX - 14GR | Toilet Rooms
| 48 Watt max | COLUMBIA - LJT14 | Provide Flange Kit
| LPW 102 min | H. E. WILLIAMS 50F
| 4000K | LA LIGHTING - 2-GHL310
| CRI 80+ / 0-10V DIMMING | MOBERN RG Series Troffers
LSI Midwest Lighting
| 2' X 4' TROFFER | LITHONIA - 2RTL4
F5 | LED | METALUX - 24AC | Corridors and Office Locations
| 38 Watt max | COLUMBIA - LEPC24
| LPW 99 max | H. E. WILLIAMS HETG
| 4000K | LSI Midwest Lighting ASC24
| CRI 80+ / 0-10V DIMMING | MOBERN - RDISD-24
| 2' X 4' RECESSED CLEAN LED | KURTZON - KL F
F6 | 116 Watt max | FAIL-SAFE - CLMG-24 | Food Service Locations
| LPW 97 min | CERTOLUX - CRG2X4
| 4000K | LA LIGHTING - 2-GCR220
| CRI 80+ / 0-10V DIMMING | PARAMOUNT INDUSTRIES, INC. G2-3
| SQUARE EXTERIOR | DESIGN PLAN - LPY
F7 | LED | KENALL - MS11FD | Exterior Covered Walkway Locations
| 32 Watt max | CGF DESIGN - BIL-WMT
| LPW 106 min | LA LIGHTING - BCL100
| 4000K | LUMINAIRE LED, Inc SWP1212
| CRI 80+ / 0-10V DIMMING | MOBERN CV304 Series Canopy Light
Eclipse Lighting Inc. QE1-B-LED
| SUSPENDED | PEERLESS LIGHTING - BRM9L
F8 | DIRECT/INDIRECT | CORELITE - J2-WL | Classroom Locations
| 53 Watt max | ALERA - LP7 | SEE PLANS FOR LENGTHS
| LPW 95 min | LumenWerx, Inc REVPSIB
| 4000K | LumenWerx, Inc REVPSIB
| CRI 80+ / 0-10V DIMMING | Mobern Linear Pendant Line
AXIS LIGHTING - SLED
CREE - S-DL6
F9 | 6" DOWNLIGHT | LITHONIA - LDN6
| LED - DOWNLIGHT | HALO COMMERCIAL - PD620 | Hallway Locations
| 24 Watt max | PRESCOLITE - LF6LEDG4
| LPW 104 min | H. E. WILLIAMS L60
| 4000K | Elco E610C
CRI 80+ / 0-10V DIMMING
| WALL BRACKET | LITHONIA - LQC
F10 | LED | METALUX - 4-BCLED | Stair Locations
| 39 Watt; max | COLUMBIA - LW
| LPW 88 min | MOBERN 1555SWS Stairwell Light
| 4000K | H. E. WILLIAMS SLF
LA LIGHTING - 3-WCP100
LSI Midwest Lighting W444
WALL WASH FIXTURE
F11 | LED | BRUCK - 137400 | Reception Areas
| 12 Watt max |  | Coordinate aiming with Art
4000k
CRI 80+ / 0-10V DIMMING
CREE - C-VT
F12 | ELEVATOR PIT LED | RAL - AVPD
| 15 Watt max | LDPI - LEVP | Elevator Pit
| LPW 110 min | HUBBELL - VWGL-1
| 4000K | PHOENIX PRODUCTS CL-13LED
| CRI 80+ / 0-10V DIMMING | DURAGUARD PRODUCTS VW43
| TRACKLIGHTS | JUNO - T261
F13 | LED | HALO - LA805MEDFL40MB277 | Platform Locations
| 18 Watt max | ELCO - ET745 | 2 Circuit Track
| LPW 62 min | ELCO - ETC45D-X
| 4000K | ELITE ET-LED-381
| CRI 80+ / 0-10V DIMMING | WAC LIGHTING L-1014
| STRIPLIGHT | LITHONIA - ZL1N
F14 | LED | METALUX - 4TSNLED | Utility, Storage, Mechanical & Electrical Rooms
| 44 Watt max | COLUMBIA - LCS8
| LPW 147 min | H. E. WILLIAMS GL-4
| 4000K | LA LIGHTING - 1-STR220
| CRI 80+ / 0-10V DIMMING | LA LIGHTING 5' LED Strip Light
MOBERN 42 Series Strip Light
LSI Midwest Lighting S-4-LED
| STRIPLIGHT LENSED | LITHONIA - ZL1D
F15 | LED | METALUX AP SERIES - 4SLSTP4040DD | Utility, Storage, Mechanical & Electrical Rooms
| 45 Watt max | COLUMBIA - LCL4
| LPW 119 min | CREE LS4
| 4000K | LA Lighting 4' LED Strip Light
| CRI 80+ / 0-10V DIMMING | MOBERN 42 Series Strip Light
LSI Midwest Lighting SDL
| INDUSTRIAL LED | LITHONIA - IBH
F16 | LINEAR LOWBAY | METALUX - 4ILED | Multipurpose Room (Low Bay)
| 121 Watt max | COLUMBIA - LLHV4
| LPW 102 min | H. E. WILLIAMS GL-4
| 4000K | LA LIGHTING - 3-HBN100
| CRI 80+ / 0-10V DIMMING | MOBERN FHBC Series High Bay
LSI Midwest Lighting XLHB
| WALLMOUNTED | LITHONIA - DSXW2
F17 | LED SCONCE | VISIONAIRE LIGHTING - VSC | Exteior Wall Mounted Sconces
| 113 Watt max | KIM - WD18D4E35
| LPW 120 min | CREE - SEC-EDG
| 4000K | US ARCHITECTURAL RAR-WM2
| CRI 80+ / 0-10V DIMMING | NLS Wall/Ceiling/Flood Light Line
GE LIGHTING SYSTEMS EWN
| 6" DOWNLIGHT | LITHONIA - LDN6 40/20 LO6WR VOLTAGE
F18 | LED | HALO COMMERICAL - PD620ED010-PDM6A840-61VW | Exterior Wet Location Downlights
| 22 Watt max | PRESCOLITE - LF6LEDG4 | WET LISTED
| LPW 95 min | ELCO - EL6LF
| 4000K | ELCO - E610L
| CRI 80+ / 0-10V DIMMING | H. E. WILLIAMS L60
F19 | WALL PACK | TECHLIGHT - LHMWP-F20
| WATTS VARY PER LAY OUT | NLS RHC | Exterior use
| LPW 85 min | SOLERA -Mini
4000K / 0-10V DIMMING
| EXIT SIGN | ACTIVE SAFETY - 2002L-BE16
X1W | SINGLE/DOUBLE FACE | ISOLITE - TL-AC-R | Exterior Wet Locations
| 6 Watt max | BEGHELLI LIGHTING - PX-A-G-SA
EVENLITE - RZR-AC-R
EELP, INC. CAHAU-1/2-G-B
EMERGI-LITE INC. **-SVX-*-R-4X
| LED Exit Lighting | Green LED is preferred. Photoluminescent Exit Signs are not to be used. | CCSD has moved away from photoluminescent because there are some specific requirements for a charging light to be within a certain distance from them, and unless they are egress lights, we cannot guarantee they will be on to charge them.
26 53 00 | Exit Signs | Big Beam ,Isolite, Kenall, Lithonia, Active Safety, Evenlite | See also 26 51 13, LED Exit Lighting
| Photoluminescent Types | Active Safety, Brady, SafeSIGN | See 26 51 13, CCSD no longer wishes to use this type of exit sign.
26 55 53 | Security Lighting
26 55 59 | Display Lighting
26 55 61 | Theatrical Lighting | Theatrical & Stage Lighting System:Strand Lighting Co., Electronic Theatre Controls, Leviton/Colortran
26 56 00 | Exterior Lighting |  | Lights must operate and function to CCSD performance specification.
26 56 13 | Lighting Poles & Standards
26 56 16 | Parking Lighting | New Construction shall be provided with LED Parking Lot Lighting: LED Lighting Packages are being developed as part of several new prototype schools. Fixture Head for Parking Lot Lighting to be mounted at 28-feet above finish grade. Approved Fixtures are as follows: | Motion Sensor Requirements: McGraw-Edison Galleon with integrated motion sensors or approved equal. In addition, install one motion sensor at each driveway entrance, to detect cars entering the property. Sensors to be aimed so they are not activated by pedestrians on sidewalks or off the property; or cars on the community streets. One additional motion sensor is to be located in a position to detect a custodian or other CCSD individual leaving by the door with a security keypad. Parking lot lighting and motion sensors to be wired to the Parking Lot Lighting Control Panel controlled by EMS.
| POLE MOUNTED | LITHONA - DSX1
S1 | PARKING LOT LIGHTING | COOPER LIGHTING - GLEON | Parking Locations
| WATTS VARY PER LAY-OUT | BEACON - VP-L
| LPW 93 min | CREE OSQ
| 4000K | CREE - OSQ
| 0-10V DIMMING | GE LIGHTING SYSTEMS EASC
NLS-STARVIEW
NLS-STARVIEW
| POLE MOUNTED | LITHONA - DSX1
S2 | DOUBLE HEADED | COOPER LIGHTING - GLEON | Parking Locations
| PARKING LOT LIGHTING; Rotate Optics. | BEACON - VP-L
| WATTS VARY PER LAYOUT | CREE (2) OSQ
| LPW 93 min | CREE - OSQ
| 4000K | GE LIGHTING SYSTEMS
0-10V DIMMING
| POLE MOUNTED | LITHONIA - DSX1
S3 | DOUBLE HEADED | COOPER LIGHTING - GLEON | Parking Locations
| PARKING LOT LIGHTING; Rotate Optics. | BEACON - VP-L
| WATTS VARY PER LAYOUT | CREE (2)OSQ
| LPW 93 min | CREE - OSQ
| 4000K 0-10V DIMMMING | GE LIGHTING SYSTEMS EASC
26 56 29 | School Perimeter Lighting Site Lighting (Includes Wall Sconces) | School perimeter wall lighting is to be wired to the Building Perimeter Lighting control Panel controlled by EMS.
| AREA LIGHTING WATTS VARY PER LAY OUT LPW min 114; 4000k; 0-10 Dimming | NLS - NV SERIES - TYPE B; B1; S2; S3 NV-1 NV-2 Poles: SSSP
26 56 33 | Walkway Lighting | See section 26 56 29
26 56 68 | Exterior Athletic Lighting | Systems: Qualite, Musco, General Electric, Hubbell Poles:Valmont, Ameron, Union Metal | Lights must operate and function to CCSD performance specification.
27 | COMMUNICATIONS
27 00 00 | Communications | AN RCDD PROFESSIONAL MUST BE DEDICATED T0 THE DESIGN & INSPECTION OF EVERY CCSD PROJECT FOR COMPLIANCE TO STANDARDS AND ANY MORE STRINGENT INSTALLATION PRACTICES AS OUTLINED IN CCSD's GUIDE SPECIFICATIONS. Design & Construction must meet TIA standards, that are in place to insure compliance to IEEE. | For modernization projects please contact Steve Adair, CCSD Networking Services. Please refer to appendix sections 27 00 00 Communications; 27 11 00 Communications Equipment Rooms &Telecomminications Rooms; 27 11 19 Communication Termination Blocks and Patch Panels; 27 13 00 Communications Backbone Cabling; 27 15 00 Communications Horizontal Cabling; 27 15 43 Communications Faceplates & Connectors; for detailed communications requirements. These sections may or may not be available with the 02/15/16 issue of this document.
27 00 00 | Grounding & Bonding | Bus Bars, Straps, Lugs, & Assoc. Fittings: Chatsworth (or approved equal proposed by Contractor)
Primary protectors with secondary transient voltage protection for exposed copper cabling: Circa
Flex Tray: Chatsworth, B-Line
Surface Raceway: Wiremold
Fabric Innerduct: MaxCel
27 10 00 | STRUCTURED CABLING
27 11 00 | Communications Equipment & Telecommunication Rooms | Cabinets, two post racks, Telecommunication Enclosures (TE), ladder tray and associated fittings: Chatsworth
Fiber Optic Raceway: ADC
27 11 19 | Communications Termination Blocks & Patch Panel | Category 6 UTP patch panels, fiber optic rack mount and wall mount patch panels, patch cords: Commscope-Systimax, Commscope-ADC Krone, Leviton (only approved with Berk-Tek cabling), Siemon
Catetory 6A-F/UTP (shielded) patch panels and patch cords: Commscope-Systimax, Siemon
27 13 00 | Communications Backbone | Multimode 50/125 laser optimized OM3 and OM4 fiber optic cable (multiples of 12-strand) for data:Commscope – Systimax, Commscope – ADC Krone, Berk-Tek (only approved with Leviton connectivity), Siemon
27 15 00 | Communications Horizontal Cabling | Category 6 UTP for Data and VoIP: Commscope-Systimax, Commscope-ADC Krone, Berk-Tek (only approve with Leviton connectivity), Siemon
Category 6A F/UTP (shielded) for wireless locations: Commscope – Systimax, Siemon
27 15 43 | Communications Faceplates & Connectors | Category 6 UTP jacks and faceplates: Commscope-Systimax, Commscope-ADC Krone, Leviton (only approved with Berk-Tek cabling), Siemon
Fiber patch panels, fiber optic connectors: Commscope-Systimax, Commscope-ADC Krone, Leviton (only approved with Berk-Tek cabling), Siemon
Category 6A F/UTP (Shielded) jacks and associated faceplates: Commscope – Systimax, Siemon
27 20 00 | DATA COMMUNICATIONS
27 26 00 | Data Communications Programming & Integration Services | Multi-System Integration Platform (MSIP): Tridium required for HVAC Systems
27 30 00 | VOICE COMMUNICATIONS
See information in other sections, Above
27 40 00 | AUDIO-VIDEO COMMUNICATIONS
27 41 00 | Audio-Video Systems
27 41 16.51 | Audio-Video Equipment | Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector (Hitachi) and Finger Touch Unit. Approved Projector - Hitachi Ultra-Short Throw Interactive (Smart) Projector: Model No. HITCPTW2505 (2700 Lumens); Model No. HITCPTW3005 (3300 Lumens). Projector Accessories: Finger Touch Module (#HITFT01); Super Booster USB Extender (#CBT29341); Wall Mounting Bracket (#HAS-WM05) | An integrated Audio Video system is currently being reviewed to include integration of the Audio-Video equipment with a 360-degree lesson capture/security camera, an wearable emergency alert/microphone device worn by a teacher, and integration with the intercom system (paging, bells, and intercom communications), with attachment to an Analog type clock. This section may be included in the Design Manual - refer to appendix section 27 51 23 IP Intercommunication System - Classroom Descreet Personal Alert, Classroom Audio/Visual Control; along with Section 27 53 13 - Clock Systems; Code Issue: The Fire and Life Safety system has to be completely independent of an integrated AV System.
27 41 16.51 | Classroom Audio-Video Equipment & Equipment | Basis of Design for Classrooms - Audio Enhancement Audio System (Alternative for Crestron): Ceiling mounted Controller/Amp: Audio Enhancement GL-300 with 8 button wall mounted controls., Audio Enhancement (TLD-100) infrared receiver; 4 ea. speakers (CS-12) connected to GL-300. Teacher Microphone: Wireless AE Teardrop (MTD09), Student Microphone: AE wireless Handheld Microphone (MHH09), 24 VDC Power Supply, Microphone, Battery Charger and rechargable batteries; along with additional wall plates, cabling, and runners listed below - to form a complete system. Classroom Front Row System - Audio System (Alternative for Crestron): Receiver: Symbio 5201R Receiver w/power supply, adapter cable, RJ45-RJ45 adapter, UTP Cat 5e cable Networked Encoder/Decoder/Amplifier: #CM800S, Conductor IP-based paging to small conference & office spaces, converts analog PA to IP-based streaming solution, Onboard GUI Software, executes pre-programmed actions such as turning off devices, password protect. Teacher microphone: wireless 940TM Transmitter & Microphone w/Smart Charge NiMH rechargeable battery, aux-in cable, boom mic. Student Pass Around Microphone & Drop-in Charger: 950H student microphone w/ 950C SmartCharge NiMH rechargeable battery (for both teacher & student microphones), charger power supply, lavaliere clip. Accessories: Decora PW-PC Wall Plate - connects computer to projector and amplifier, CB50 Volume Control with 4-pin connector with bridging to the CB2000. Distributed Ceiling Speaker and sensors, & EZROOM Enclosures, along with additional wall plates, cabling, and runners to form a complete system. Additional "or equal" Manufacturers: Crestron, Extron | Refer to Appendix 27 41 16.51 for additional Audio Video Equipment and systems information. Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector.
27 41 16.51 | Classroom Wall Plate & Cabling for 8 Button Wall Plate at Teacher Station | 8-Button Teacher Control Wall Plate: Audio Enhancement No. SP Controls Pixie Plus Wall Plate. Cabling: RTC Module; RS-232 Unidirectional Output to GL300; RS 232 Port #2; Front Row "or equal" Wall Plate/Cables; Additional "or equal" Manufacturers: Crestron, Extron | Refer to Appendix 27 41 16.51 for additional Audio Video Equipment and systems information. Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector.
27 41 16.51 | Classroom A/V Connection Wall Plate & Cabling | A/V Connection Wall Plate: Audio Enhancement Wall Plate: RapidRun HDMI, VGA, Stereo Audio, Composite Video and Audio Double Gang Wall Plate Transmitter w/One Keystone - Aluminum -(60134). Cabling: 1 ea. VGA Video Input; 1 ea. Audio Imput, 1 ea. HDMI Input; 1 ea. Composite Video & L/R Audio Input; Front Row "or equal" Wall Plate/Cabling; Additional "or equal" Manufacturers: Crestron, Extron | Refer to Appendix 27 41 16.51 for additional Audio Video Equipment and systems information. Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector.
27 41 16.51 | Classroom AV Connection Runners - Direct to Projector | AV Connection to Projector: Audio Enhancement - 1 ea. Rapid Run Multi-Format Plenum Runner (Length as Needed); 1.5-foot Runner Rapid Run VGA (HD15) +3.5mm + Composite Video +Stereo Audio Flying Lead (60018), 1 ea. Rapid Run Optical Runner Cable - Plenum, OFNP-Rated (Length as Needed), 1 ea. Rapid Run HDMI Receiver Flying Lead, 1 ea. Composite Video & L/R Audio Input; Front Row "or equal" AV Connection Runners to Projector; Additional "or equal" Manufacturers: Crestron, Extron | Refer to Appendix 27 41 16.51 for additional Audio Video Equipment and systems information. Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector.
27 41 16.51 | AV Vendor-Furnished Boxed Set of Cables per Room | Boxed Set of Cables: 1 ea. HDMI Male to HDMI Male 10-foot Cable; 1 ea. Mini HDMI Male to Female HDMI Adapter; 1 ea. DVI Male to (2) ea VGA Female Cable; 1 ea. VGA Male to Male Cable; 1 ea. 3.5mm Male to Male Audio Cable; 1 ea. Liberty 3 RCA M-M, 10-foot cable; 1 ea. Mini-DVI to VGA Adapter for MAC; 2 ea. 3-foot VGA Cables; 1 ea. SXGA Monitor Y-Cable For Dell Computers Video Adapter Y: Trip-Lite P120-001-2 Lenovo Computers: Display Port Adapter Part no. 57Y4393 | Refer to Appendix 27 41 16.51 for Audio Video Equipment; and systems information. Include any related equipment, along with additional wall plates, cabling, and runners to form a complete system. Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector.
27 41 16.51 | Classroom Secondary A/V Connection Wall Plate & Cabling (May be Optional) | Secondary AV Connection Wall Plate: Audio Enhancement Rapid Run VGA (HD15) +3.5mm Decora Style Wall Plate - White-60054; Cabling: 1 ea. VGA Video Input, 1 ea. Audio Input, 1.5-foot Rapid Run VGA (HD15) Right Angle +3.5mm Flying Lead - 60066, Soft Rapid Run Multi-Format Runner Cable - Plenum CMP-Rated-Optimized for High Density, Multi-Format Signal Applications over a single Cable - 60013; Front Row "or equal" Wall Plate/Cables; Additional "or equal" Manufacturers: Crestron, Extron | Refer to Appendix 27 41 16.51 for additional Audio Video Equipment and systems information. Refer to section 11 52 16 for integration of the Audio System with the Ultra-Short Throw Smart Projector.
27 41 16.51a | Audio-Video Systems & Equipment for Theaters | Refer to Appendix 27 41 16.51 for Audio Video Equipment; and systems information. System appropriate for Multipurpose Room and Stage Configuration. System appropriate for Multipurpose Room and Stage Configuration. | Connect and integrate Audio system to Public Address System. Use PA microphones. Include equipment, speakers, amps, controllers, microphones along with additional wall plates, cabling, and runners to form a complete system.
27 41 16.51b | Audio-Video Systems & Equipment for Multipurpose Room and Stage | Refer to Appendix 27 41 16.51 for Audio Video Equipment; and systems information. System appropriate for Multipurpose Room and Stage Configuration. | The location of the projectors may change in the Multi-purpose room and may also be located "behind the Multipurpose screen"; up on the stage for classroom use. Floor locations for electrical plugs are not preferred because of the difficulty in cleaning the floor; including the mop water that may damage the device itself. Include equipment, speakers, amps, controllers, microphones along with additional wall plates, cabling, and runners to form a complete system.
27 41 16.51c | Audio-Video Systems & Equipment for Office Conference Room | Audio Enhancement Controller/Amp:GL-300 with 8 button wall mounted controls.; 2 ea. speakers (CS-12) connected to GL-300; include wall plates, cabling, and runners for a complete system. Front Row "or equal" Wall Plate/Cables; Additional "or equal" Manufacturers: Crestron, Extron | Refer to Appendix 27 41 16.51 for Audio Video Equipment; and systems information. Include any related equipment, along with additional wall plates, cabling, and runners to form a complete system.
27 41 33 | Master Antenna Television Systems | BTV/EBS SYSTEM Antennas: VHF Broadband: Blonder-Tongue BTY-LP-BB; Amplifiers: VHF Broadband: Blonder-Tongue RMDA 550-30; | UHF is not used anymore
28 | ELECTRONIC SAFETY & SECURITY
28 01 00 | Operation & Maintenance of Electronic Security
28 05 00 | Common Work Results for Electronic Safety and Security
| CCTV Communications Conductors and Cables | CCTV System: Sony Security
28 10 00 | Electronic Access Control and Intrusion Detection
28 11 00 | Equipment Room / Telecommunications Room Installation Requirements | Equipment Room/Telecommunications Room: Standing and Wall Mount Cabinets: Chatsworth Primary Racks: Chatsworth Cable Management: ADC / Krone, Chatsworth, Panduit Grounding and Bonding: Chatsworth Wire Partition: L.K. Goodwin Ceiling Enclosures: Chatsworth
28 13 00 | Access Control
28 16 00 | Intrusion Detection | System: DSC Intrusion Alarm Edge Devices: Honeywell – Tradeline; United Technology Company – GE Sentrol; Visonic Copper Cable: ADC / Krone (Tyco) , Belden, Coleman Cable , West Penn Transformers and Relays: Altronix Intrusion Alarm Enclosures: United Technologies Company – GE Alliance Alarm Batteries: Yuasa Cabeling: Cat6 (ADC / Krone, Tyco) Cable Termination/Management: 3M Scotchlok, Ideal, Arlington, Gardner Bender, Panduit, Hellerman Tyton | Guide Specifications and Design Guidelines are provided by CCSD Security Department, please review CCSD Design Manual
28 20 00 | Electronic Surveillance
28 23 23 | Video Surveillance Systems Infrastructure | Camera Mounting Hardware: Indoor-Ceiling Open Frame Kit: Part # YTICB45 Gooseneck Wall Mount Bracket: Part # UNIWMB4 Pendant Mount Bracket: Part # UNIMDPDVM772 Corner Mount Adapter: Part # UNICMA1 Pendant Bracket: Part # UNIMDB3 Pole Mount Adapter: Part # UNIPMA1 Power Supply: OFCI Copper Cable: ADC / Krone (Tyco), West Penn Wire Fiber Optic Cable: ADC / Krone (Tyco) Copper Connectivity: Siemon, Ideal Fiber Connectivity: Siemon Cable Management: Siemon, Panduit Uninterrruptible Power Supply: OFOI Video Balun: OFCI Video Management System used at CCSD- Milestone | All cameras modules are Owner Furnished, Contractor Installed (OFCI). Fixed camera, mounting plates, and factory camera patch cables. Specifications and Design Guidelines are provided by CCSD Security Department. Please review Appendix 28 23 23 and other related sections within the CCSD Design Manual.
28 30 00 | Electronic Detection and Alarm
28 31 00 | Fire Detection and Alarm | Overall Fire Alarm System Fire Alarm Systems: Gamewell - FCI (Fire Control Instruments) by Honeywell, Notifier by Honeywell - NSF2-640, NSF2-3030; Potter Signal/Wheelock New Schools: Provide speaker systems as part of the Fire Alarm System per NFPA 72, 2013 International Fire Code to meet voice evacuation and intelligibility requirements and State Fire Marshall regulations. MC Cable: is acceptable for use in all locations except where it is visible to the publie (i.e. where the ceiling is open to the structure). Voice Evacuation Panel: Notifier by Honeywell #NFC-50/100(E) First Command (Basis of Design); Similar product - FCI by Honeywell | Modernization Projects: Schools without a voice-evac system need to be evaluated on a case by case basis. Any variance request must be reviewed by the State Fire Marshall for each individual school.
28 31 46 | Smoke Detection Sensor System | System Sensor must be Aspirating Type, compatible with Notifier and FCI. | This item is to be used only in large computer rooms with a high volume of computer and technology equipment (i.e. specialized Computer Teaching Rooms, High School Head End Rooms/Equipment Room).
32 | EXTERIOR IMPROVEMENTS
32 18 00 | Athletic & Recreational Surfacing | US Greentech: SAFESHELL (Infill for artificial turf fields)
US Greentech: Envirofill (Infill for synthetic turf fields)
32 18 16 | Synthetic Resilient Surfacing | Playground Protective Surfacing: Gflex by Evans Recreation Inc – Basis of Design ;Tot Turf by Robertson Industries; Flexground Poured in Place surfacing by Flexground Herbicide Treatment: Ciba-Geigy Corporation; Dow Chemical USA; E.I. DuPont de Nemours & Co.; U.S. Borax and Chemical Corp. | Manufacturer to provide 10 yr warranty. Re-seal after 5 years. Use concrete slurry base under play surfacing. Require IPEMA Certified Imact Attenuation. Mfgr’s certified installer to have 5 yrs. documented experience. 10 year warranty for workmanship and materials - repair or replace defective surfacing; 5 year warranty for maintenance cushion layer and wear surface replacement.
32 18 23 | Athletic Surfacing | Asphaltic Concrete Paving and Color Finish System for Tennis courts: The Laykold Acrylic Color System as manufactured by Advanced Polymer Technology; The Plexipave System by California Products Game Co. System as manufactured by General Acrylics; The Nova Surface System by Nova USA, TPS 5000 Court Surfaces by Hellas Construction. Running Track Paving, Urethane Base Mat, and structural spray Surfacing: PolyMat by Atlas Track and Tennis Sports Track 200 by Hellas Construction; Cal Trax M by California Track and Engineering; RSS-1000 by Renner Sports Running Track Urethane Base Mat Surfacing: PolyMat by Atlas Track and Tennis; Sports Track 200 by Hellas Construction; Cal Trax M by California Track and Engineering; RSS-1000 by Renner Sports; APT - Spurtan BS; Stockmeier Urethanes-Stobitan SC Structural Spray: Qualipur 5050 by Advanced Polymer Technology
32 18 26 | Artificial Grass Surfacing | AGL PRO 69 Plus
32 31 13 | Chain Link Fencing | Specify Standard non-decorative chain link fencing unless otherwise directed. | Comply with requirements of Chain Link Fence Manufacturer's Institute (CLFMI). 5 year warranty required - repair or replace components of chain-link fences and gates that fail in materials or workmanship.
32 33 43.13 | Site Seating | Prefabricated Benches and Custom Concrete Benches are allowed
32 84 00 | Irrigation Pumps | Pump Stations: Barrett; Flo-boy; Munro | Above Ground Piping going into and out of the booster pump shall be Class 51 Ductile Iron
32 84 00 | Irrigation Components | New Construction: Hydropoint Weather Trak ETPro3, 2-wire system (default watering required if WAN is down). Flow Meter: Hydropoint FLOW3 (Flow Meter - MasterValve - Submeter) Control Valves: Hydropoint FLOW3, Hunter, Rain Bird, Irritrol Isolation Valves: Clow; Kennedy; Milwaukee; Narac; Nibco; Spears Valve Boxes: Ametek; Carson; Dura Plastics Pre-Manufactured Swing Joint Assembly: Dura Plastics; Spears Bubblers: Rain Bird Quick Coupling Valves: Rain Bird, Hunter Controller’s: Modernization Projects - Existing Controllers are Acclima; Rain Bird; Rain Master; match existing system. TRC Irrigation Remote Control System for use will all existing controllers - replacement only. Modernization - Master Control Valves: Data Industrial (Flow Meters); Hunter; Griswold Controls; IrriTrol; Rain Bird; Superior Controls | Alan Paulson's department will maintain the new irrigation controllers
32 84 00 | Drip Irrigation | Netafim; Rain Bird; GPH, Salco; Senniger
32 84 00 | Irrigation - Spray & Rotor Heads | Hunter; Rain Bird
32 84 00 | Irrigation Piping | C900 for underground piping 4-inch and over: Schedule 40 PVC - up to 4-inch; Class 51 Ductile Iron
32 92 23 | Sodding | Sod: Valley Sod Farms (888-925-6675); Western Coast Turf (888-893-8873)
32 & 33 | Storm Drain, Drainage | Sports Edge: Enplast 580 Shock Drain, Rubber Curb Products, HQ Panel Drain, Permavoid Drainage System, Terminator Drainage System, XT-4 & XT-6 Drainage System
Note on B124: ====== ID#AAAAMeLpuvM Windows User (2021-06-04 15:47:20) Windows User: